## techniques
ID | STIX ID | name | description | url | created | last modified | domain | version | tactics | detection | platforms | data sources | contributors | relationship citations
T0800 | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | Activate Firmware Update Mode | Adversaries may activate firmware update mode on devices to prevent expected response functions from engaging in reaction to an emergency or process malfunction. For example, devices such as protection relays may have an operation mode designed for firmware installation. This mode may halt process monitoring and related functions to allow new firmware to be loaded. A device left in update mode may be placed in an inactive holding state if no firmware is provided to it. By entering and leaving a device in this mode, the adversary may deny its usual functionalities. | https://attack.mitre.org/techniques/T0800 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm | Joe Slowik - Dragos | (Citation: Joe Slowik August 2019),(Citation: Department of Homeland Security September 2016),
T0830 | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | Adversary-in-the-Middle | Adversaries with privileged network access may seek to modify network traffic in real time using adversary-in-the-middle (AiTM) attacks. (Citation: Gabriel Sanchez October 2017) This type of attack allows the adversary to intercept traffic to and/or from a particular device on the network. If a AiTM attack is established, then the adversary has the ability to block, log, modify, or inject traffic into the communication stream. There are several ways to accomplish this attack, but some of the most-common are Address Resolution Protocol (ARP) poisoning and the use of a proxy. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) An AiTM attack may allow an adversary to perform the following attacks: [Block Reporting Message](https://attack.mitre.org/techniques/T0804), [Spoof Reporting Message](https://attack.mitre.org/techniques/T0856), [Modify Parameter](https://attack.mitre.org/techniques/T0836), [Unauthorized Command Message](https://attack.mitre.org/techniques/T0855) | https://attack.mitre.org/techniques/T0830 | 21 May 2020 | 13 October 2023 | ics-attack | 2.0 | Collection |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation, Service: Service Creation, Windows Registry: Windows Registry Key Modification | Conrad Layne - GE Digital | (Citation: William Largent June 2018),(Citation: Triton-EENews-2017),(Citation: Carl Hurd March 2019),,
T0878 | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | Alarm Suppression | Adversaries may target protection function alarms to prevent them from notifying operators of critical conditions. Alarm messages may be a part of an overall reporting system and of particular interest for adversaries. Disruption of the alarm system does not imply the disruption of the reporting system as a whole. A Secura presentation on targeting OT notes a dual fold goal for adversaries attempting alarm suppression: prevent outgoing alarms from being raised and prevent incoming alarms from being responded to. (Citation: Jos Wetzels, Marina Krotofil 2019) The method of suppression may greatly depend on the type of alarm in question: * An alarm raised by a protocol message * An alarm signaled with I/O * An alarm bit set in a flag (and read) In ICS environments, the adversary may have to suppress or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: Jos Wetzels, Marina Krotofil 2019) Methods of suppression may involve tampering or altering device displays and logs, modifying in memory code to fixed values, or even tampering with assembly level instruction code. | https://attack.mitre.org/techniques/T0878 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Inhibit Response Function |  | None | Network Traffic: Network Traffic Flow, Operational Databases: Device Alarm, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm | Jos Wetzels - Midnight Blue; Marina Krotofil | (Citation: Marshall Abrams July 2008),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Dwight Anderson 2014),(Citation: Keith Stouffer May 2015),(Citation: Department of Homeland Security September 2016),
T0802 | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | Automated Collection | Adversaries may automate collection of industrial environment information using tools or scripts. This automated collection may leverage native control protocols and tools available in the control systems environment. For example, the OPC protocol may be used to enumerate and gather information. Access to a system or interface with these native protocols may allow collection and enumeration of other attached, communicating servers and devices. | https://attack.mitre.org/techniques/T0802 | 21 May 2020 | 05 April 2024 | ics-attack | 1.1 | Collection |  | None | Command: Command Execution, File: File Access, Network Traffic: Network Traffic Content, Script: Script Execution |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Industroyer2 Forescout July 2022),,
T0895 | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | Autorun Image | Adversaries may leverage AutoRun functionality or scripts to execute malicious code. Devices configured to enable AutoRun functionality or legacy operating systems may be susceptible to abuse of these features to run malicious code stored on various forms of removeable media (i.e., USB, Disk Images [.ISO]). Commonly, AutoRun or AutoPlay are disabled in many operating systems configurations to mitigate against this technique. If a device is configured to enable AutoRun or AutoPlay, adversaries may execute code on the device by mounting the removable media to the device, either through physical or virtual means. This may be especially relevant for virtual machine environments where disk images may be dynamically mapped to a guest system on a hypervisor. An example could include an adversary gaining access to a hypervisor through the management interface to modify a virtual machine’s hardware configuration. They could then deploy an iso image with a malicious AutoRun script to cause the virtual machine to automatically execute the code contained on the disk image. This would enable the execution of malicious code within a virtual machine without needing any prior remote access to that system. | https://attack.mitre.org/techniques/T0895 | 26 March 2024 | 08 April 2024 | ics-attack | 1.0 | Execution |  |  | Drive: Drive Creation, Process: Process Creation |  | (Citation: Mandiant-Sandworm-Ukraine-2022),,
T0803 | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | Block Command Message | Adversaries may block a command message from reaching its intended target to prevent command execution. In OT networks, command messages are sent to provide instructions to control system devices. A blocked command message can inhibit response functions from correcting a disruption or unsafe condition. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) (Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/techniques/T0803 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),,
T0804 | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | Block Reporting Message | Adversaries may block or prevent a reporting message from reaching its intended target. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. By blocking these reporting messages, an adversary can potentially hide their actions from an operator. Blocking reporting messages in control systems that manage physical processes may contribute to system impact, causing inhibition of a response function. A control system may not be able to respond in a proper or timely manner to an event, such as a dangerous fault, if its corresponding reporting message is blocked. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) (Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/techniques/T0804 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),,
T0805 | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | Block Serial COM | Adversaries may block access to serial COM to prevent instructions or configurations from reaching target devices. Serial Communication ports (COM) allow communication with control system devices. Devices can receive command and configuration messages over such serial COM. Devices also use serial COM to send command and reporting messages. Blocking device serial COM may also block command messages and block reporting messages. A serial to Ethernet converter is often connected to a serial COM to facilitate communication between serial and Ethernet devices. One approach to blocking a serial COM would be to create and hold open a TCP session with the Ethernet side of the converter. A serial to Ethernet converter may have a few ports open to facilitate multiple communications. For example, if there are three serial COM available -- 1, 2 and 3 --, the converter might be listening on the corresponding ports 20001, 20002, and 20003. If a TCP/IP connection is opened with one of these ports and held open, then the port will be unavailable for use by another party. One way the adversary could achieve this would be to initiate a TCP session with the serial to Ethernet converter at 10.0.0.1 via Telnet on serial port 1 with the following command: telnet 10.0.0.1 20001. | https://attack.mitre.org/techniques/T0805 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm, Process: Process Termination |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Booz Allen Hamilton),,
T0806 | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | Brute Force I/O | Adversaries may repetitively or successively change I/O point values to perform an action. Brute Force I/O may be achieved by changing either a range of I/O point values or a single point value repeatedly to manipulate a process function. The adversary's goal and the information they have about the target environment will influence which of the options they choose. In the case of brute forcing a range of point values, the adversary may be able to achieve an impact without targeting a specific point. In the case where a single point is targeted, the adversary may be able to generate instability on the process function associated with that particular point. Adversaries may use Brute Force I/O to cause failures within various industrial processes. These failures could be the result of wear on equipment or damage to downstream equipment. | https://attack.mitre.org/techniques/T0806 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impair Process Control |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Process History/Live Data |  | (Citation: Industroyer2 Mandiant April 2022),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Industroyer2 Forescout July 2022),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Dwight Anderson 2014),(Citation: Keith Stouffer May 2015),(Citation: Department of Homeland Security September 2016),
T0892 | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | Change Credential | Adversaries may modify software and device credentials to prevent operator and responder access. Depending on the device, the modification or addition of this password could prevent any device configuration actions from being accomplished and may require a factory reset or replacement of hardware. These credentials are often built-in features provided by the device vendors as a means to restrict access to management interfaces. An adversary with access to valid or hardcoded credentials could change the credential to prevent future authorized device access. Change Credential may be especially damaging when paired with other techniques such as Modify Program, Data Destruction, or Modify Controller Tasking. In these cases, a device’s configuration may be destroyed or include malicious actions for the process environment, which cannot not be removed through normal device configuration actions. Additionally, recovery of the device and original configuration may be difficult depending on the features provided by the device. In some cases, these passwords cannot be removed onsite and may require that the device be sent back to the vendor for additional recovery steps. A chain of incidents occurred in Germany, where adversaries locked operators out of their building automation system (BAS) controllers by enabling a previously unset BCU key. (Citation: German BAS Lockout Dec 2021) | https://attack.mitre.org/techniques/T0892 | 30 March 2023 | 13 October 2023 | ics-attack | 1.0 | Inhibit Response Function |  | None | Network Traffic: Network Traffic Content, Operational Databases: Device Alarm | Felix Eberstaller | ,(Citation: CISA June 2013),(Citation: Department of Homeland Security October 2009),(Citation: M. Rentschler and H. Heine),
T0858 | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | Change Operating Mode | Adversaries may change the operating mode of a controller to gain additional access to engineering functions such as Program Download. Programmable controllers typically have several modes of operation that control the state of the user program and control access to the controllers API. Operating modes can be physically selected using a key switch on the face of the controller but may also be selected with calls to the controllers API. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic. [Program Upload](https://attack.mitre.org/techniques/T0845) and [Program Download](https://attack.mitre.org/techniques/T0843) are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) | https://attack.mitre.org/techniques/T0858 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Evasion, Execution |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Wylie-22),(Citation: MDudek-ICS),(Citation: Dragos-Pipedream),(Citation: Department of Homeland Security September 2016),
T0807 | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | Command-Line Interface | Adversaries may utilize command-line interfaces (CLIs) to interact with systems and execute commands. CLIs provide a means of interacting with computer systems and are a common feature across many types of platforms and devices within control systems environments. (Citation: Enterprise ATT&CK January 2018) Adversaries may also use CLIs to install and run new software, including malicious tools that may be installed over the course of an operation. CLIs are typically accessed locally, but can also be exposed via services, such as SSH, Telnet, and RDP. Commands that are executed in the CLI execute with the current permissions level of the process running the terminal emulator, unless the command specifies a change in permissions context. Many controllers have CLI interfaces for management purposes. | https://attack.mitre.org/techniques/T0807 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Execution |  | None | Application Log: Application Log Content, Command: Command Execution, Process: Process Creation |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: FireEye TRITON Dec 2017),(Citation: Mandiant-Sandworm-Ukraine-2022),(Citation: Dragos October 2018),(Citation: ESET Industroyer),,
T0885 | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | Commonly Used Port | Adversaries may communicate over a commonly used port to bypass firewalls or network detection systems and to blend in with normal network activity, to avoid more detailed inspection. They may use the protocol associated with the port, or a completely different protocol. They may use commonly open ports, such as the examples provided below. * TCP:80 (HTTP) * TCP:443 (HTTPS) * TCP/UDP:53 (DNS) * TCP:1024-4999 (OPC on XP/Win2k3) * TCP:49152-65535 (OPC on Vista and later) * TCP:23 (TELNET) * UDP:161 (SNMP) * TCP:502 (MODBUS) * TCP:102 (S7comm/ISO-TSAP) * TCP:20000 (DNP3) * TCP:44818 (Ethernet/IP) | https://attack.mitre.org/techniques/T0885 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Command and Control |  | None | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow | Matan Dobrushin - Otorio | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: MDudek-ICS),(Citation: Booz Allen Hamilton),(Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014),
T0884 | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | Connection Proxy | Adversaries may use a connection proxy to direct network traffic between systems or act as an intermediary for network communications. The definition of a proxy can also be expanded to encompass trust relationships between networks in peer-to-peer, mesh, or trusted connections between networks consisting of hosts or systems that regularly communicate with each other. The network may be within a single organization or across multiple organizations with trust relationships. Adversaries could use these types of relationships to manage command and control communications, to reduce the number of simultaneous outbound network connections, to provide resiliency in the face of connection loss, or to ride over existing trusted communications paths between victims to avoid suspicion. (Citation: Enterprise ATT&CK January 2018) | https://attack.mitre.org/techniques/T0884 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Command and Control |  | None | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow |  | (Citation: Wylie-22),(Citation: Dragos Inc. June 2017),(Citation: Booz Allen Hamilton),(Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014),
T0879 | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | Damage to Property | Adversaries may cause damage and destruction of property to infrastructure, equipment, and the surrounding environment when attacking control systems. This technique may result in device and operational equipment breakdown, or represent tangential damage from other techniques used in an attack. Depending on the severity of physical damage and disruption caused to control processes and systems, this technique may result in [Loss of Safety](https://attack.mitre.org/techniques/T0880). Operations that result in [Loss of Control](https://attack.mitre.org/techniques/T0827) may also cause damage to property, which may be directly or indirectly motivated by an adversary seeking to cause impact in the form of [Loss of Productivity and Revenue](https://attack.mitre.org/techniques/T0828). The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill under an incidents affecting business section of its 2014 IT Security Report. (Citation: BSI State of IT Security 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact and damage resulted from the uncontrolled shutdown of a blast furnace. A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) (Citation: Bruce Schneier January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. This resulted in damage to impacted trams, people, and the surrounding property. Reportedly, four trams were derailed and were forced to make emergency stops. (Citation: Shelley Smith February 2008) Commands issued by the student may have also resulted in tram collisions, causing harm to those on board and the environment outside. (Citation: Bruce Schneier January 2008) | https://attack.mitre.org/techniques/T0879 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impact |  | None |  |  | (Citation: Marshall Abrams July 2008),(Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004),(Citation: Department of Homeland Security September 2016),
T0809 | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | Data Destruction | Adversaries may perform data destruction over the course of an operation. The adversary may drop or create malware, tools, or other non-native files on a target system to accomplish this, potentially leaving behind traces of malicious activities. Such non-native files and other data may be removed over the course of an intrusion to maintain a small footprint or as a standard part of the post-intrusion cleanup process. (Citation: Enterprise ATT&CK January 2018) Data destruction may also be used to render operator interfaces unable to respond and to disrupt response functions from occurring as expected. An adversary may also destroy data backups that are vital to recovery after an incident. Standard file deletion commands are available on most operating system and device interfaces to perform cleanup, but adversaries may use other tools as well. Two examples are Windows Sysinternals SDelete and Active@ Killdisk. | https://attack.mitre.org/techniques/T0809 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Inhibit Response Function |  | None | Command: Command Execution, File: File Deletion, File: File Modification, Process: Process Creation | Matan Dobrushin - Otorio | (Citation: Dragos-Pipedream),(Citation: Dragos Inc. June 2017),(Citation: Brubaker-Incontroller),(Citation: Wylie-22),(Citation: Anton Cherepanov),(Citation: National Institute of Standards and Technology April 2013),
T0811 | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | Data from Information Repositories | Adversaries may target and collect data from information repositories. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Examples of information repositories include reference databases in the process environment, as well as databases in the corporate network that might contain information about the ICS.(Citation: Cybersecurity & Infrastructure Security Agency March 2018) Information collected from these systems may provide the adversary with a better understanding of the operational environment, vendors used, processes, or procedures of the ICS. In a campaign between 2011 and 2013 against ONG organizations, Chinese state-sponsored actors searched document repositories for specific information such as, system manuals, remote terminal unit (RTU) sites, personnel lists, documents that included the string SCAD*, user credentials, and remote dial-up access information. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/techniques/T0811 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Collection |  | None | Application Log: Application Log Content, Logon Session: Logon Session Creation, Network Share: Network Share Access |  | (Citation: Symantec),(Citation: Keith Stouffer May 2015),(Citation: National Institute of Standards and Technology April 2013),
T0893 | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | Data from Local System | Adversaries may target and collect data from local system sources, such as file systems, configuration files, or local databases. This can include sensitive data such as specifications, schematics, or diagrams of control system layouts, devices, and processes. Adversaries may do this using [Command-Line Interface](https://attack.mitre.org/techniques/T0807) or [Scripting](https://attack.mitre.org/techniques/T0853) techniques to interact with the file system to gather information. Adversaries may also use [Automated Collection](https://attack.mitre.org/techniques/T0802) on the local system. | https://attack.mitre.org/techniques/T0893 | 30 March 2023 | 09 April 2024 | ics-attack | 1.0 | Collection |  | None | Command: Command Execution, File: File Access, Process: OS API Execution, Process: Process Creation, Script: Script Execution |  | (Citation: Kevin Savage and Branko Spasojevic),(Citation: Symantec),(Citation: ESET),(Citation: Keith Stouffer May 2015),(Citation: National Institute of Standards and Technology April 2013),
T0812 | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | Default Credentials | Adversaries may leverage manufacturer or supplier set default credentials on control system devices. These default credentials may have administrative permissions and may be necessary for initial configuration of the device. It is general best practice to change the passwords for these accounts as soon as possible, but some manufacturers may have devices that have passwords or usernames that cannot be changed. (Citation: Keith Stouffer May 2015) Default credentials are normally documented in an instruction manual that is either packaged with the device, published online through official means, or published online through unofficial means. Adversaries may leverage default credentials that have not been properly modified or disabled. | https://attack.mitre.org/techniques/T0812 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Lateral Movement |  | None | Logon Session: Logon Session Creation, Network Traffic: Network Traffic Content |  | (Citation: CISA Unitronics November 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),,
T0813 | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | Denial of Control | Adversaries may cause a denial of control to temporarily prevent operators and engineers from interacting with process controls. An adversary may attempt to deny process control access to cause a temporary loss of communication with the control device or to prevent operator adjustment of process controls. An affected process may still be operating during the period of control loss, but not necessarily in a desired state. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) In the 2017 Dallas Siren incident operators were unable to disable the false alarms from the Office of Emergency Management headquarters. (Citation: Mark Loveless April 2017) | https://attack.mitre.org/techniques/T0813 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impact |  | None |  |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),(Citation: Marshall Abrams July 2008),(Citation: Booz Allen Hamilton),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0814 | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | Denial of Service | Adversaries may perform Denial-of-Service (DoS) attacks to disrupt expected device functionality. Examples of DoS attacks include overwhelming the target device with a high volume of requests in a short time period and sending the target device a request it does not know how to handle. Disrupting device state may temporarily render it unresponsive, possibly lasting until a reboot can occur. When placed in this state, devices may be unable to send and receive requests, and may not perform expected response functions in reaction to other events in the environment. Some ICS devices are particularly sensitive to DoS events, and may become unresponsive in reaction to even a simple ping sweep. Adversaries may also attempt to execute a Permanent Denial-of-Service (PDoS) against certain devices, such as in the case of the BrickerBot malware. (Citation: ICS-CERT April 2017) Adversaries may exploit a software vulnerability to cause a denial of service by taking advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Vulnerabilities may exist in software that can be used to cause a denial of service condition. Adversaries may have prior knowledge about industrial protocols or control devices used in the environment through [Remote System Information Discovery](https://attack.mitre.org/techniques/T0888). There are examples of adversaries remotely causing a [Device Restart/Shutdown](https://attack.mitre.org/techniques/T0816) by exploiting a vulnerability that induces uncontrolled resource consumption. (Citation: ICS-CERT August 2018) (Citation: Common Weakness Enumeration January 2019) (Citation: MITRE March 2018) | https://attack.mitre.org/techniques/T0814 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: WPXI Aliquippa Water November 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),(Citation: Frank Bajak and Marc Levy December 2023),(Citation: ICS-CERT August 2018),(Citation: Ukraine15 - EISAC - 201603),(Citation: CISA Unitronics November 2023),,
T0815 | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | Denial of View | Adversaries may cause a denial of view in attempt to disrupt and prevent operator oversight on the status of an ICS environment. This may manifest itself as a temporary communication failure between a device and its control source, where the interface recovers and becomes available once the interference ceases. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) An adversary may attempt to deny operator visibility by preventing them from receiving status and reporting messages. Denying this view may temporarily block and prevent operators from noticing a change in state or anomalous behavior. The environment's data and processes may still be operational, but functioning in an unintended or adversarial manner. | https://attack.mitre.org/techniques/T0815 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impact |  | None |  |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Marshall Abrams July 2008),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0868 | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | Detect Operating Mode | Adversaries may gather information about a PLCs or controllers current operating mode. Operating modes dictate what change or maintenance functions can be manipulated and are often controlled by a key switch on the PLC (e.g., run, prog [program], and remote). Knowledge of these states may be valuable to an adversary to determine if they are able to reprogram the PLC. Operating modes and the mechanisms by which they are selected often vary by vendor and product line. Some commonly implemented operating modes are described below: * Program - This mode must be enabled before changes can be made to a devices program. This allows program uploads and downloads between the device and an engineering workstation. Often the PLCs logic Is halted, and all outputs may be forced off. (Citation: N.A. October 2017) * Run - Execution of the devices program occurs in this mode. Input and output (values, points, tags, elements, etc.) are monitored and used according to the programs logic.[Program Upload](https://attack.mitre.org/techniques/T0845) and [Program Download](https://attack.mitre.org/techniques/T0843) are disabled while in this mode. (Citation: Omron) (Citation: Machine Information Systems 2007) (Citation: N.A. October 2017) (Citation: PLCgurus 2021) * Remote - Allows for remote changes to a PLCs operation mode. (Citation: PLCgurus 2021) * Stop - The PLC and program is stopped, while in this mode, outputs are forced off. (Citation: Machine Information Systems 2007) * Reset - Conditions on the PLC are reset to their original states. Warm resets may retain some memory while cold resets will reset all I/O and data registers. (Citation: Machine Information Systems 2007) * Test / Monitor mode - Similar to run mode, I/O is processed, although this mode allows for monitoring, force set, resets, and more generally tuning or debugging of the system. Often monitor mode may be used as a trial for initialization. (Citation: Omron) | https://attack.mitre.org/techniques/T0868 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Collection |  | None | Network Traffic: Network Traffic Content |  | (Citation: MDudek-ICS),(Citation: Department of Homeland Security September 2016),
T0816 | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | Device Restart/Shutdown | Adversaries may forcibly restart or shutdown a device in an ICS environment to disrupt and potentially negatively impact physical processes. Methods of device restart and shutdown exist in some devices as built-in, standard functionalities. These functionalities can be executed using interactive device web interfaces, CLIs, and network protocol commands. Unexpected restart or shutdown of control system devices may prevent expected response functions happening during critical states. A device restart can also be a sign of malicious device modifications, as many updates require a shutdown in order to take effect. | https://attack.mitre.org/techniques/T0816 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Device Alarm |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),(Citation: Booz Allen Hamilton),(Citation: Department of Homeland Security September 2016),
T0817 | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | Drive-by Compromise | Adversaries may gain access to a system during a drive-by compromise, when a user visits a website as part of a regular browsing session. With this technique, the user's web browser is targeted and exploited simply by visiting the compromised website. The adversary may target a specific community, such as trusted third party suppliers or other industry specific groups, which often visit the target website. This kind of targeted attack relies on a common interest, and is known as a strategic web compromise or watering hole attack. The National Cyber Awareness System (NCAS) has issued a Technical Alert (TA) regarding Russian government cyber activity targeting critical infrastructure sectors. (Citation: Cybersecurity & Infrastructure Security Agency March 2018) Analysis by DHS and FBI has noted two distinct categories of victims in the Dragonfly campaign on the Western energy sector: staging and intended targets. The adversary targeted the less secure networks of staging targets, including trusted third-party suppliers and related peripheral organizations. Initial access to the intended targets used watering hole attacks to target process control, ICS, and critical infrastructure related trade publications and informational websites. | https://attack.mitre.org/techniques/T0817 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access |  | None | Application Log: Application Log Content, File: File Creation, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Content, Process: Process Creation |  | (Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017),(Citation: Chris Bing May 2018),(Citation: Eduard Kovacs May 2018),(Citation: Symantec Security Response July 2014),,
T0871 | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | Execution through API | Adversaries may attempt to leverage Application Program Interfaces (APIs) used for communication between control software and the hardware. Specific functionality is often coded into APIs which can be called by software to engage specific functions on a device or other software. | https://attack.mitre.org/techniques/T0871 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Execution |  | None | Process: OS API Execution |  | (Citation: Jos Wetzels January 2018),(Citation: MITRE June 2020),(Citation: McCarthy, J et al. July 2018),
T0819 | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | Exploit Public-Facing Application | Adversaries may leverage weaknesses to exploit internet-facing software for initial access into an industrial network. Internet-facing software may be user applications, underlying networking implementations, an assets operating system, weak defenses, etc. Targets of this technique may be intentionally exposed for the purpose of remote management and visibility. An adversary may seek to target public-facing applications as they may provide direct access into an ICS environment or the ability to move into the ICS network. Publicly exposed applications may be found through online tools that scan the internet for open ports and services. Version numbers for the exposed application may provide adversaries an ability to target specific known vulnerabilities. Exposed control protocol or remote access ports found in Commonly Used Port may be of interest by adversaries. | https://attack.mitre.org/techniques/T0819 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content |  | (Citation: ICS CERT September 2018),(Citation: ICS-CERT December 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Keith Stouffer May 2015),(Citation: National Institute of Standards and Technology April 2013),
T0820 | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | Exploitation for Evasion | Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to evade detection. Vulnerabilities may exist in software that can be used to disable or circumvent security features. Adversaries may have prior knowledge through [Remote System Information Discovery](https://attack.mitre.org/techniques/T0888) about security features implemented on control devices. These device security features will likely be targeted directly for exploitation. There are examples of firmware RAM/ROM consistency checks on control devices being targeted by adversaries to enable the installation of malicious [System Firmware](https://attack.mitre.org/techniques/T0857). | https://attack.mitre.org/techniques/T0820 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Evasion |  | None | Application Log: Application Log Content |  | (Citation: The Office of Nuclear Reactor Regulation),(Citation: Schneider Electric January 2018),(Citation: ICS-CERT December 2018),(Citation: DHS CISA February 2019),(Citation: Microsoft Security Response Center August 2017),(Citation: Wikipedia),(Citation: Dan Goodin March 2017),
T0890 | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | Exploitation for Privilege Escalation | Adversaries may exploit software vulnerabilities in an attempt to elevate privileges. Exploitation of a software vulnerability occurs when an adversary takes advantage of a programming error in a program, service, or within the operating system software or kernel itself to execute adversary-controlled code. Security constructs such as permission levels will often hinder access to information and use of certain techniques, so adversaries will likely need to perform privilege escalation to include use of software exploitation to circumvent those restrictions. (Citation: The MITRE Corporation) When initially gaining access to a system, an adversary may be operating within a lower privileged process which will prevent them from accessing certain resources on the system. Vulnerabilities may exist, usually in operating system components and software commonly running at higher permissions, that can be exploited to gain higher levels of access on the system. This could enable someone to move from unprivileged or user level permissions to SYSTEM or root permissions depending on the component that is vulnerable. This may be a necessary step for an adversary compromising an endpoint system that has been properly configured and limits other privilege escalation methods. (Citation: The MITRE Corporation) | https://attack.mitre.org/techniques/T0890 | 13 April 2021 | 13 October 2023 | ics-attack | 1.1 | Privilege Escalation |  | None | Application Log: Application Log Content |  | (Citation: Wylie-22),(Citation: DHS CISA February 2019),(Citation: Microsoft Security Response Center August 2017),(Citation: Wikipedia),(Citation: Dan Goodin March 2017),
T0866 | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | Exploitation of Remote Services | Adversaries may exploit a software vulnerability to take advantage of a programming error in a program, service, or within the operating system software or kernel itself to enable remote service abuse. A common goal for post-compromise exploitation of remote services is for initial access into and lateral movement throughout the ICS environment to enable access to targeted systems. (Citation: Enterprise ATT&CK) ICS asset owners and operators have been affected by ransomware (or disruptive malware masquerading as ransomware) migrating from enterprise IT to ICS environments: WannaCry, NotPetya, and BadRabbit. In each of these cases, self-propagating (wormable) malware initially infected IT networks, but through exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks, producing significant impacts. (Citation: Joe Slowik April 2019) | https://attack.mitre.org/techniques/T0866 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access, Lateral Movement |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content |  | (Citation: Joe Slowik April 2019),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Keith Stouffer May 2015),(Citation: Microsoft Security Response Center August 2017),(Citation: Wikipedia),(Citation: Dan Goodin March 2017),
T0822 | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | External Remote Services | Adversaries may leverage external remote services as a point of initial access into your network. These services allow users to connect to internal network resources from external locations. Examples are VPNs, Citrix, and other access mechanisms. Remote service gateways often manage connections and credential authentication for these services. (Citation: Daniel Oakley, Travis Smith, Tripwire) External remote services allow administration of a control system from outside the system. Often, vendors and internal engineering groups have access to external remote services to control system networks via the corporate network. In some cases, this access is enabled directly from the internet. While remote access enables ease of maintenance when a control system is in a remote area, compromise of remote access solutions is a liability. The adversary may use these services to gain access to and execute attacks against a control system network. Access to valid accounts is often a requirement. As they look for an entry point into the control system network, adversaries may begin searching for existing point-to-point VPN implementations at trusted third party networks or through remote support employee connections where split tunneling is enabled. (Citation: Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016) | https://attack.mitre.org/techniques/T0822 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Initial Access |  | None | Application Log: Application Log Content, Logon Session: Logon Session Metadata, Network Traffic: Network Traffic Flow |  | (Citation: Marshall Abrams July 2008),(Citation: Booz Allen Hamilton),(Citation: Keith Stouffer May 2015),(Citation: Department of Homeland Security September 2016),
T0823 | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | Graphical User Interface | Adversaries may attempt to gain access to a machine via a Graphical User Interface (GUI) to enhance execution capabilities. Access to a GUI allows a user to interact with a computer in a more visual manner than a CLI. A GUI allows users to move a cursor and click on interface objects, with a mouse and keyboard as the main input devices, as opposed to just using the keyboard. If physical access is not an option, then access might be possible via protocols such as VNC on Linux-based and Unix-based operating systems, and RDP on Windows operating systems. An adversary can use this access to execute programs and applications on the target machine. | https://attack.mitre.org/techniques/T0823 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Execution |  | None | Command: Command Execution, Logon Session: Logon Session Creation, Module: Module Load, Process: Process Creation |  | (Citation: Ukraine15 - EISAC - 201603),,
T0891 | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | Hardcoded Credentials | Adversaries may leverage credentials that are hardcoded in software or firmware to gain an unauthorized interactive user session to an asset. Examples credentials that may be hardcoded in an asset include: * Username/Passwords * Cryptographic keys/Certificates * API tokens Unlike [Default Credentials](https://attack.mitre.org/techniques/T0812), these credentials are built into the system in a way that they either cannot be changed by the asset owner, or may be infeasible to change because of the impact it would cause to the control system operation. These credentials may be reused across whole product lines or device models and are often not published or known to the owner and operators of the asset. Adversaries may utilize these hardcoded credentials to move throughout the control system environment or provide reliable access for their tools to interact with industrial assets. | https://attack.mitre.org/techniques/T0891 | 29 September 2022 | 13 October 2023 | ics-attack | 1.0 | Lateral Movement, Persistence |  | None | Logon Session: Logon Session Creation, Network Traffic: Network Traffic Content | Aagam Shah, @neutrinoguy, ABB | (Citation: Wylie-22),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),,
T0874 | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | Hooking | Adversaries may hook into application programming interface (API) functions used by processes to redirect calls for execution and privilege escalation means. Windows processes often leverage these API functions to perform tasks that require reusable system resources. Windows API functions are typically stored in dynamic-link libraries (DLLs) as exported functions. (Citation: Enterprise ATT&CK) One type of hooking seen in ICS involves redirecting calls to these functions via import address table (IAT) hooking. IAT hooking uses modifications to a process IAT, where pointers to imported API functions are stored. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | https://attack.mitre.org/techniques/T0874 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Execution, Privilege Escalation |  | None | Process: OS API Execution, Process: Process Metadata |  | (Citation: Jos Wetzels January 2018),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),,
T0877 | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | I/O Image | Adversaries may seek to capture process values related to the inputs and outputs of a PLC. During the scan cycle, a PLC reads the status of all inputs and stores them in an image table. (Citation: Nanjundaiah, Vaidyanath) The image table is the PLCs internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. The Input and Output Image tables described above make up the I/O Image on a PLC. This image is used by the user program instead of directly interacting with physical I/O. (Citation: Spenneberg, Ralf 2016) Adversaries may collect the I/O Image state of a PLC by utilizing a devices [Native API](https://attack.mitre.org/techniques/T0834) to access the memory regions directly. The collection of the PLCs I/O state could be used to replace values or inform future stages of an attack. | https://attack.mitre.org/techniques/T0877 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Collection |  | None | Asset: Software |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),,
T0872 | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | Indicator Removal on Host | Adversaries may attempt to remove indicators of their presence on a system in an effort to cover their tracks. In cases where an adversary may feel detection is imminent, they may try to overwrite, delete, or cover up changes they have made to the device. | https://attack.mitre.org/techniques/T0872 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Evasion |  | None | Command: Command Execution, File: File Deletion, File: File Metadata, File: File Modification, Process: OS API Execution, Process: Process Creation, Windows Registry: Windows Registry Key Deletion, Windows Registry: Windows Registry Key Modification |  | (Citation: Jos Wetzels January 2018),(Citation: Anton Cherepanov),(Citation: FireEye TRITON Dec 2017),(Citation: Keith Stouffer May 2015),(Citation: National Institute of Standards and Technology April 2013),
T0883 | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | Internet Accessible Device | Adversaries may gain access into industrial environments through systems exposed directly to the internet for remote access rather than through [External Remote Services](https://attack.mitre.org/techniques/T0822). Internet Accessible Devices are exposed to the internet unintentionally or intentionally without adequate protections. This may allow for adversaries to move directly into the control system network. Access onto these devices is accomplished without the use of exploits, these would be represented within the [Exploit Public-Facing Application](https://attack.mitre.org/techniques/T0819) technique. Adversaries may leverage built in functions for remote access which may not be protected or utilize minimal legacy protections that may be targeted. (Citation: NCCIC January 2014) These services may be discoverable through the use of online scanning tools. In the case of the Bowman dam incident, adversaries leveraged access to the dam control network through a cellular modem. Access to the device was protected by password authentication, although the application was vulnerable to brute forcing. (Citation: NCCIC January 2014) (Citation: Danny Yadron December 2015) (Citation: Mark Thompson March 2016) In Trend Micros manufacturing deception operations adversaries were detected leveraging direct internet access to an ICS environment through the exposure of operational protocols such as Siemens S7, Omron FINS, and EtherNet/IP, in addition to misconfigured VNC access. (Citation: Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rsler, and Rainer Vosseler) | https://attack.mitre.org/techniques/T0883 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access |  | None | Logon Session: Logon Session Metadata, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow |  | (Citation: Lisa Zahner December 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),,
T0867 | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | Lateral Tool Transfer | Adversaries may transfer tools or other files from one system to another to stage adversary tools or other files over the course of an operation. (Citation: Enterprise ATT&CK) Copying of files may also be performed laterally between internal victim systems to support Lateral Movement with remote Execution using inherent file sharing protocols such as file sharing over SMB to connected network shares. (Citation: Enterprise ATT&CK) In control systems environments, malware may use SMB and other file sharing protocols to move laterally through industrial networks. | https://attack.mitre.org/techniques/T0867 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Lateral Movement |  | None | Command: Command Execution, File: File Creation, File: File Metadata, Network Share: Network Share Access, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Booz Allen Hamilton),(Citation: CISA-AA22-103A),(Citation: FireEye TEMP.Veles 2018),(Citation: Dragos Crashoverride 2018),(Citation: Wylie-22),(Citation: Joe Slowik April 2019),(Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014),
T0826 | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | Loss of Availability | Adversaries may attempt to disrupt essential components or systems to prevent owner and operator from delivering products or services. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) Adversaries may leverage malware to delete or encrypt critical data on HMIs, workstations, or databases. In the 2021 Colonial Pipeline ransomware incident, pipeline operations were temporally halted on May 7th and were not fully restarted until May 12th. (Citation: Colonial Pipeline Company May 2021) | https://attack.mitre.org/techniques/T0826 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Catalin Cimpanu April 2016),(Citation: Ukraine15 - EISAC - 201603),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: Booz Allen Hamilton),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0827 | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | Loss of Control | Adversaries may seek to achieve a sustained loss of control or a runaway condition in which operators cannot issue any commands even if the malicious interference has subsided. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) The German Federal Office for Information Security (BSI) reported a targeted attack on a steel mill in its 2014 IT Security Report.(Citation: BSI State of IT Security 2014) These targeted attacks affected industrial operations and resulted in breakdowns of control system components and even entire installations. As a result of these breakdowns, massive impact resulted in damage and unsafe conditions from the uncontrolled shutdown of a blast furnace. | https://attack.mitre.org/techniques/T0827 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  | Dragos Threat Intelligence | (Citation: Kevin Beaumont),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),(Citation: Hydro),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0828 | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | Loss of Productivity and Revenue | Adversaries may cause loss of productivity and revenue through disruption and even damage to the availability and integrity of control system operations, devices, and related processes. This technique may manifest as a direct effect of an ICS-targeting attack or tangentially, due to an IT-targeting attack against non-segregated environments. In cases where these operations or services are brought to a halt, the loss of productivity may eventually present an impact for the end-users or consumers of products and services. The disrupted supply-chain may result in supply shortages and increased prices, among other consequences. A ransomware attack on an Australian beverage company resulted in the shutdown of some manufacturing sites, including precautionary halts to protect key systems. (Citation: Paganini, Pierluigi June 2020) The company announced the potential for temporary shortages of their products following the attack. (Citation: Paganini, Pierluigi June 2020) (Citation: Lion Corporation June 2020) In the 2021 Colonial Pipeline ransomware incident, the pipeline was unable to transport approximately 2.5 million barrels of fuel per day to the East Coast. (Citation: Colonial Pipeline Company May 2021) | https://attack.mitre.org/techniques/T0828 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Kevin Beaumont),(Citation: Kelly Jackson Higgins),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: Booz Allen Hamilton),(Citation: FireEye TRITON Dec 2017),(Citation: Catalin Cimpanu April 2016),(Citation: Marc-Etienne M.Lveill October 2017),(Citation: Davey Winder June 2020),(Citation: David Voreacos, Katherine Chinglinsky, Riley Griffin December 2019),(Citation: Hydro),(Citation: Ukraine15 - EISAC - 201603),(Citation: Selena Larson, Camille Singleton December 2020),(Citation: Department of Homeland Security October 2009),
T0837 | attack-pattern--2bb4d762-bf4a-4bc3-9318-15cc6a354163 | Loss of Protection | Adversaries may compromise protective system functions designed to prevent the effects of faults and abnormal conditions. This can result in equipment damage, prolonged process disruptions and hazards to personnel. Many faults and abnormal conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable protective system functions as a prerequisite to subsequent attack execution or to allow for future faults and abnormal conditions to go unchecked. Detection of a Loss of Protection by operators can result in the shutdown of a process due to strict policies regarding protection systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. | https://attack.mitre.org/techniques/T0837 | 12 April 2021 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Joe Slowik August 2019),,
T0880 | attack-pattern--5fa00fdd-4a55-4191-94a0-564181d7fec2 | Loss of Safety | Adversaries may compromise safety system functions designed to maintain safe operation of a process when unacceptable or dangerous conditions occur. Safety systems are often composed of the same elements as control systems but have the sole purpose of ensuring the process fails in a predetermined safe manner. Many unsafe conditions in process control happen too quickly for a human operator to react to. Speed is critical in correcting these conditions to limit serious impacts such as Loss of Control and Property Damage. Adversaries may target and disable safety system functions as a prerequisite to subsequent attack execution or to allow for future unsafe conditionals to go unchecked. Detection of a Loss of Safety by operators can result in the shutdown of a process due to strict policies regarding safety systems. This can cause a Loss of Productivity and Revenue and may meet the technical goals of adversaries seeking to cause process disruptions. | https://attack.mitre.org/techniques/T0880 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017),(Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004),
T0829 | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | Loss of View | Adversaries may cause a sustained or permanent loss of view where the ICS equipment will require local, hands-on operator intervention; for instance, a restart or manual operation. By causing a sustained reporting or visibility loss, the adversary can effectively hide the present state of operations. This loss of view can occur without affecting the physical processes themselves. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) | https://attack.mitre.org/techniques/T0829 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Kevin Beaumont),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: Booz Allen Hamilton),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),(Citation: Hydro),(Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013),(Citation: M. Rentschler and H. Heine),
T0835 | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | Manipulate I/O Image | Adversaries may manipulate the I/O image of PLCs through various means to prevent them from functioning as expected. Methods of I/O image manipulation may include overriding the I/O table via direct memory manipulation or using the override function used for testing PLC programs. (Citation: Dr. Kelvin T. Erickson December 2010) During the scan cycle, a PLC reads the status of all inputs and stores them in an image table. (Citation: Nanjundaiah, Vaidyanath) The image table is the PLCs internal storage location where values of inputs/outputs for one scan are stored while it executes the user program. After the PLC has solved the entire logic program, it updates the output image table. The contents of this output image table are written to the corresponding output points in I/O Modules. One of the unique characteristics of PLCs is their ability to override the status of a physical discrete input or to override the logic driving a physical output coil and force the output to a desired status. | https://attack.mitre.org/techniques/T0835 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Asset: Software |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),,
T0831 | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | Manipulation of Control | Adversaries may manipulate physical process control within the industrial environment. Methods of manipulating control can include changes to set point values, tags, or other parameters. Adversaries may manipulate control systems devices or possibly leverage their own, to communicate with and command physical control processes. The duration of manipulation may be temporary or longer sustained, depending on operator detection. Methods of Manipulation of Control include: * Man-in-the-middle * Spoof command message * Changing setpoints A Polish student used a remote controller device to interface with the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) (Citation: Bruce Schneier January 2008) Using this remote, the student was able to capture and replay legitimate tram signals. As a consequence, four trams were derailed and twelve people injured due to resulting emergency stops. (Citation: Shelley Smith February 2008) The track controlling commands issued may have also resulted in tram collisions, a further risk to those on board and nearby the areas of impact. (Citation: Bruce Schneier January 2008) | https://attack.mitre.org/techniques/T0831 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Ukraine15 - EISAC - 201603),(Citation: Department of Homeland Security October 2009),
T0832 | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | Manipulation of View | Adversaries may attempt to manipulate the information reported back to operators or controllers. This manipulation may be short term or sustained. During this time the process itself could be in a much different state than what is reported. (Citation: Corero) (Citation: Michael J. Assante and Robert M. Lee) (Citation: Tyson Macaulay) Operators may be fooled into doing something that is harmful to the system in a loss of view situation. With a manipulated view into the systems, operators may issue inappropriate control sequences that introduce faults or catastrophic failures into the system. Business analysis systems can also be provided with inaccurate data leading to bad management decisions. | https://attack.mitre.org/techniques/T0832 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Langer Stuxnet),(Citation: Department of Homeland Security October 2009),
T0849 | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | Masquerading | Adversaries may use masquerading to disguise a malicious application or executable as another file, to avoid operator and engineer suspicion. Possible disguises of these masquerading files can include commonly found programs, expected vendor executables and configuration files, and other commonplace application and naming conventions. By impersonating expected and vendor-relevant files and applications, operators and engineers may not notice the presence of the underlying malicious content and possibly end up running those masquerading as legitimate functions. Applications and other files commonly found on Windows systems or in engineering workstations have been impersonated before. This can be as simple as renaming a file to effectively disguise it in the ICS environment. | https://attack.mitre.org/techniques/T0849 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Evasion |  | None | Command: Command Execution, File: File Metadata, File: File Modification, Process: Process Metadata, Scheduled Job: Scheduled Job Creation, Scheduled Job: Scheduled Job Modification, Service: Service Creation, Service: Service Modification |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Tom Fakterman August 2019),(Citation: DHS CISA February 2019),(Citation: Dragos Threat Intelligence February 2020),(Citation: FireEye TRITON),(Citation: Dragos Crashoverride 2018),,
T0838 | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | Modify Alarm Settings | Adversaries may modify alarm settings to prevent alerts that may inform operators of their presence or to prevent responses to dangerous and unintended scenarios. Reporting messages are a standard part of data acquisition in control systems. Reporting messages are used as a way to transmit system state information and acknowledgements that specific actions have occurred. These messages provide vital information for the management of a physical process, and keep operators, engineers, and administrators aware of the state of system devices and physical processes. If an adversary is able to change the reporting settings, certain events could be prevented from being reported. This type of modification can also prevent operators or devices from performing actions to keep the system in a safe state. If critical reporting messages cannot trigger these actions then a [Impact](https://attack.mitre.org/tactics/TA0105) could occur. In ICS environments, the adversary may have to use [Alarm Suppression](https://attack.mitre.org/techniques/T0878) or contend with multiple alarms and/or alarm propagation to achieve a specific goal to evade detection or prevent intended responses from occurring. (Citation: Jos Wetzels, Marina Krotofil 2019) Methods of suppression often rely on modification of alarm settings, such as modifying in memory code to fixed values or tampering with assembly level instruction code. | https://attack.mitre.org/techniques/T0838 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Inhibit Response Function |  | None | Application Log: Application Log Content, Asset: Asset Inventory, Network Traffic: Network Traffic Content, Operational Databases: Process History/Live Data |  | (Citation: Marshall Abrams July 2008),(Citation: N/A),(Citation: Department of Homeland Security September 2016),
T0821 | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | Modify Controller Tasking | Adversaries may modify the tasking of a controller to allow for the execution of their own programs. This can allow an adversary to manipulate the execution flow and behavior of a controller. According to 61131-3, the association of a Task with a Program Organization Unit (POU) defines a task association. (Citation: IEC February 2013) An adversary may modify these associations or create new ones to manipulate the execution flow of a controller. Modification of controller tasking can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Tasks have properties, such as interval, frequency and priority to meet the requirements of program execution. Some controller vendors implement tasks with implicit, pre-defined properties whereas others allow for these properties to be formulated explicitly. An adversary may associate their program with tasks that have a higher priority or execute associated programs more frequently. For instance, to ensure cyclic execution of their program on a Siemens controller, an adversary may add their program to the task, Organization Block 1 (OB1). | https://attack.mitre.org/techniques/T0821 | 13 April 2021 | 13 October 2023 | ics-attack | 1.2 | Execution |  | None | Application Log: Application Log Content, Asset: Software, Operational Databases: Device Alarm |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Jos Wetzels January 2018),(Citation: DHS CISA February 2019),(Citation: IEC February 2019),
T0836 | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | Modify Parameter | Adversaries may modify parameters used to instruct industrial control system devices. These devices operate via programs that dictate how and when to perform actions based on such parameters. Such parameters can determine the extent to which an action is performed and may specify additional options. For example, a program on a control system device dictating motor processes may take a parameter defining the total number of seconds to run that motor. An adversary can potentially modify these parameters to produce an outcome outside of what was intended by the operators. By modifying system and process critical parameters, the adversary may cause [Impact](https://attack.mitre.org/tactics/TA0105) to equipment and/or control processes. Modified parameters may be turned into dangerous, out-of-bounds, or unexpected values from typical operations. For example, specifying that a process run for more or less time than it should, or dictating an unusually high, low, or invalid value as a parameter. | https://attack.mitre.org/techniques/T0836 | 21 May 2020 | 13 October 2023 | ics-attack | 1.3 | Impair Process Control |  | None | Application Log: Application Log Content, Asset: Asset Inventory, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Industroyer2 Mandiant April 2022),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Industroyer2 Forescout July 2022),(Citation: Wylie-22),(Citation: Marshall Abrams July 2008),(Citation: PLCTop20 Mar 2023),
T0889 | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | Modify Program | Adversaries may modify or add a program on a controller to affect how it interacts with the physical process, peripheral devices and other hosts on the network. Modification to controller programs can be accomplished using a Program Download in addition to other types of program modification such as online edit and program append. Program modification encompasses the addition and modification of instructions and logic contained in Program Organization Units (POU) (Citation: IEC February 2013) and similar programming elements found on controllers. This can include, for example, adding new functions to a controller, modifying the logic in existing functions and making new calls from one function to another. Some programs may allow an adversary to interact directly with the native API of the controller to take advantage of obscure features or vulnerabilities. | https://attack.mitre.org/techniques/T0889 | 13 April 2021 | 20 October 2023 | ics-attack | 1.2 | Persistence |  | None | Application Log: Application Log Content, Asset: Software, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: IEC February 2019),
T0839 | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | Module Firmware | Adversaries may install malicious or vulnerable firmware onto modular hardware devices. Control system devices often contain modular hardware devices. These devices may have their own set of firmware that is separate from the firmware of the main control system equipment. This technique is similar to [System Firmware](https://attack.mitre.org/techniques/T0857), but is conducted on other system components that may not have the same capabilities or level of integrity checking. Although it results in a device re-image, malicious device firmware may provide persistent access to remaining devices. (Citation: Daniel Peck, Dale Peterson January 2009) An easy point of access for an adversary is the Ethernet card, which may have its own CPU, RAM, and operating system. The adversary may attack and likely exploit the computer on an Ethernet card. Exploitation of the Ethernet card computer may enable the adversary to accomplish additional attacks, such as the following: (Citation: Daniel Peck, Dale Peterson January 2009) * Delayed Attack - The adversary may stage an attack in advance and choose when to launch it, such as at a particularly damaging time. * Brick the Ethernet Card - Malicious firmware may be programmed to result in an Ethernet card failure, requiring a factory return. * Random Attack or Failure - The adversary may load malicious firmware onto multiple field devices. Execution of an attack and the time it occurs is generated by a pseudo-random number generator. * A Field Device Worm - The adversary may choose to identify all field devices of the same model, with the end goal of performing a device-wide compromise. * Attack Other Cards on the Field Device - Although it is not the most important module in a field device, the Ethernet card is most accessible to the adversary and malware. Compromise of the Ethernet card may provide a more direct route to compromising other modules, such as the CPU module. | https://attack.mitre.org/techniques/T0839 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Impair Process Control, Persistence |  | None | Application Log: Application Log Content, Firmware: Firmware Modification, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | ,(Citation: Intel),(Citation: N/A),(Citation: ESET Research Whitepapers September 2018),(Citation: Department of Homeland Security September 2016),
T0801 | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | Monitor Process State | Adversaries may gather information about the physical process state. This information may be used to gain more information about the process itself or used as a trigger for malicious actions. The sources of process state information may vary such as, OPC tags, historian data, specific PLC block information, or network traffic. | https://attack.mitre.org/techniques/T0801 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Collection |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Industroyer2 Forescout July 2022),,
T0834 | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | Native API | Adversaries may directly interact with the native OS application programming interface (API) to access system functions. Native APIs provide a controlled means of calling low-level OS services within the kernel, such as those involving hardware/devices, memory, and processes. (Citation: The MITRE Corporation May 2017) These native APIs are leveraged by the OS during system boot (when other system components are not yet initialized) as well as carrying out tasks and requests during routine operations. Functionality provided by native APIs are often also exposed to user-mode applications via interfaces and libraries. For example, functions such as memcpy and direct operations on memory registers can be used to modify user and system memory space. | https://attack.mitre.org/techniques/T0834 | 13 April 2021 | 13 October 2023 | ics-attack | 1.0 | Execution |  | None | Process: OS API Execution |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Jos Wetzels January 2018),,
T0840 | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | Network Connection Enumeration | Adversaries may perform network connection enumeration to discover information about device communication patterns. If an adversary can inspect the state of a network connection with tools, such as Netstat(Citation: Netstat), in conjunction with [System Firmware](https://attack.mitre.org/techniques/T0857), then they can determine the role of certain devices on the network (Citation: MITRE). The adversary can also use [Network Sniffing](https://attack.mitre.org/techniques/T0842) to watch network traffic for details about the source, destination, protocol, and content. | https://attack.mitre.org/techniques/T0840 | 21 May 2020 | 29 March 2024 | ics-attack | 1.2 | Discovery |  | None | Command: Command Execution, Process: OS API Execution, Process: Process Creation, Script: Script Execution |  | (Citation: Anton Cherepanov, ESET June 2017),(Citation: Ben Hunter and Fred Gutierrez July 2020),,
T0842 | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | Network Sniffing | Network sniffing is the practice of using a network interface on a computer system to monitor or capture information (Citation: Enterprise ATT&CK January 2018) regardless of whether it is the specified destination for the information. An adversary may attempt to sniff the traffic to gain information about the target. This information can vary in the level of importance. Relatively unimportant information is general communications to and from machines. Relatively important information would be login information. User credentials may be sent over an unencrypted protocol, such as Telnet, that can be captured and obtained through network packet analysis. In addition, ARP and Domain Name Service (DNS) poisoning can be used to capture credentials to websites, proxies, and internal systems by redirecting traffic to an adversary. | https://attack.mitre.org/techniques/T0842 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Discovery |  | None | Command: Command Execution, Process: Process Creation |  | (Citation: William Largent June 2018),(Citation: Wylie-22),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Carl Hurd March 2019),(Citation: Keith Stouffer May 2015),(Citation: National Institute of Standards and Technology April 2013),
T0861 | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | Point & Tag Identification | Adversaries may collect point and tag values to gain a more comprehensive understanding of the process environment. Points may be values such as inputs, memory locations, outputs or other process specific variables. (Citation: Dennis L. Sloatman September 2016) Tags are the identifiers given to points for operator convenience. Collecting such tags provides valuable context to environmental points and enables an adversary to map inputs, outputs, and other values to their control processes. Understanding the points being collected may inform an adversary on which processes and values to keep track of over the course of an operation. | https://attack.mitre.org/techniques/T0861 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Collection |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content | Jos Wetzels - Midnight Blue | (Citation: ICS-CERT August 2018),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: CISA-AA22-103A),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Dwight Anderson 2014),(Citation: Keith Stouffer May 2015),(Citation: Department of Homeland Security September 2016),
T0843 | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | Program Download | Adversaries may perform a program download to transfer a user program to a controller. Variations of program download, such as online edit and program append, allow a controller to continue running during the transfer and reconfiguration process without interruption to process control. However, before starting a full program download (i.e., download all) a controller may need to go into a stop state. This can have negative consequences on the physical process, especially if the controller is not able to fulfill a time-sensitive action. Adversaries may choose to avoid a download all in favor of an online edit or program append to avoid disrupting the physical process. An adversary may need to use the technique Detect Operating Mode or Change Operating Mode to make sure the controller is in the proper mode to accept a program download. The granularity of control to transfer a user program in whole or parts is dictated by the management protocol (e.g., S7CommPlus, TriStation) and underlying controller API. Thus, program download is a high-level term for the suite of vendor-specific API calls used to configure a controllers user program memory space. [Modify Controller Tasking](https://attack.mitre.org/techniques/T0821) and [Modify Program](https://attack.mitre.org/techniques/T0889) represent the configuration changes that are transferred to a controller via a program download. | https://attack.mitre.org/techniques/T0843 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Lateral Movement |  | None | Application Log: Application Log Content, Asset: Asset Inventory, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: FireEye TRITON Dec 2017),(Citation: Jos Wetzels January 2018),(Citation: Brubaker-Incontroller),(Citation: Wylie-22),(Citation: IEC February 2019),(Citation: Department of Homeland Security September 2016),
T0845 | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | Program Upload | Adversaries may attempt to upload a program from a PLC to gather information about an industrial process. Uploading a program may allow them to acquire and study the underlying logic. Methods of program upload include vendor software, which enables the user to upload and read a program running on a PLC. This software can be used to upload the target program to a workstation, jump box, or an interfacing device. | https://attack.mitre.org/techniques/T0845 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Collection |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow |  | (Citation: Wylie-22),(Citation: Brubaker-Incontroller),(Citation: MDudek-ICS),(Citation: Department of Homeland Security September 2016),
T0873 | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | Project File Infection | Adversaries may attempt to infect project files with malicious code. These project files may consist of objects, program organization units, variables such as tags, documentation, and other configurations needed for PLC programs to function. (Citation: Beckhoff) Using built in functions of the engineering software, adversaries may be able to download an infected program to a PLC in the operating environment enabling further [Execution](https://attack.mitre.org/tactics/TA0104) and [Persistence](https://attack.mitre.org/tactics/TA0110) techniques. (Citation: PLCdev) Adversaries may export their own code into project files with conditions to execute at specific intervals. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) Malicious programs allow adversaries control of all aspects of the process enabled by the PLC. Once the project file is downloaded to a PLC the workstation device may be disconnected with the infected project file still executing. (Citation: PLCdev) | https://attack.mitre.org/techniques/T0873 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Persistence |  | None | File: File Modification |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: National Institute of Standards and Technology April 2013),
T0886 | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | Remote Services | Adversaries may leverage remote services to move between assets and network segments. These services are often used to allow operators to interact with systems remotely within the network, some examples are RDP, SMB, SSH, and other similar mechanisms. (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) (Citation: Dragos December 2017) (Citation: Joe Slowik April 2019) Remote services could be used to support remote access, data transmission, authentication, name resolution, and other remote functions. Further, remote services may be necessary to allow operators and administrators to configure systems within the network from their engineering or management workstations. An adversary may use this technique to access devices which may be dual-homed (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) to multiple network segments, and can be used for [Program Download](https://attack.mitre.org/techniques/T0843) or to execute attacks on control devices directly through [Valid Accounts](https://attack.mitre.org/techniques/T0859). Specific remote services (RDP & VNC) may be a precursor to enable [Graphical User Interface](https://attack.mitre.org/techniques/T0823) execution on devices such as HMIs or engineering workstation software. Based on incident data, CISA and FBI assessed that Chinese state-sponsored actors also compromised various authorized remote access channels, including systems designed to transfer data and/or allow access between corporate and ICS networks. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/techniques/T0886 | 12 April 2021 | 13 October 2023 | ics-attack | 1.1 | Initial Access, Lateral Movement |  | None | Command: Command Execution, Logon Session: Logon Session Creation, Module: Module Load, Network Share: Network Share Access, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Flow, Process: Process Creation | Daisuke Suzuki | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Dragos-Pipedream),(Citation: Max Heinemeyer February 2020),(Citation: Andy Greenberg June 2017),(Citation: Triton-EENews-2017),(Citation: Dragos Crashoverride 2018),(Citation: Brubaker-Incontroller),(Citation: FireEye TRITON 2018),(Citation: Wylie-22),(Citation: North America Transmission Forum December 2019),
T0846 | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | Remote System Discovery | Adversaries may attempt to get a listing of other systems by IP address, hostname, or other logical identifier on a network that may be used for subsequent Lateral Movement or Discovery techniques. Functionality could exist within adversary tools to enable this, but utilities available on the operating system or vendor software could also be used. (Citation: Enterprise ATT&CK January 2018) | https://attack.mitre.org/techniques/T0846 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Discovery |  | None | File: File Access, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation |  | (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016),(Citation: Charles McLellan March 2016),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Dragos-Pipedream),(Citation: Booz Allen Hamilton),(Citation: CISA-AA22-103A),(Citation: Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell December 2015),(Citation: DHS CISA February 2019),(Citation: Wylie-22),(Citation: D. Parsons and D. Wylie September 2019),(Citation: Langner November 2018),(Citation: Josh Rinaldi April 2016),(Citation: Colin Gray),(Citation: Aditya K Sood July 2019),
T0888 | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | Remote System Information Discovery | An adversary may attempt to get detailed information about remote systems and their peripherals, such as make/model, role, and configuration. Adversaries may use information from Remote System Information Discovery to aid in targeting and shaping follow-on behaviors. For example, the system's operational role and model information can dictate whether it is a relevant target for the adversary's operational objectives. In addition, the system's configuration may be used to scope subsequent technique usage. Requests for system information are typically implemented using automation and management protocols and are often automatically requested by vendor software during normal operation. This information may be used to tailor management actions, such as program download and system or module firmware. An adversary may leverage this same information by issuing calls directly to the system's API. | https://attack.mitre.org/techniques/T0888 | 13 April 2021 | 13 October 2023 | ics-attack | 1.1 | Discovery |  | None | File: File Access, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Process: Process Creation |  | (Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: CISA-AA22-103A),(Citation: ESET Industroyer),(Citation: Industroyer2 Forescout July 2022),(Citation: Wylie-22),(Citation: ICS-CERT August 2018),(Citation: Industroyer2 ESET April 2022),(Citation: D. Parsons and D. Wylie September 2019),(Citation: Langner November 2018),(Citation: Josh Rinaldi April 2016),(Citation: Colin Gray),(Citation: Aditya K Sood July 2019),
T0847 | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | Replication Through Removable Media | Adversaries may move onto systems, such as those separated from the enterprise network, by copying malware to removable media which is inserted into the control systems environment. The adversary may rely on unknowing trusted third parties, such as suppliers or contractors with access privileges, to introduce the removable media. This technique enables initial access to target devices that never connect to untrusted networks, but are physically accessible. Operators of the German nuclear power plant, Gundremmingen, discovered malware on a facility computer not connected to the internet. (Citation: Kernkraftwerk Gundremmingen April 2016) (Citation: Trend Micro April 2016) The malware included Conficker and W32.Ramnit, which were also found on eighteen removable disk drives in the facility. (Citation: Christoph Steitz, Eric Auchard April 2016) (Citation: Catalin Cimpanu April 2016) (Citation: Peter Dockrill April 2016) (Citation: Lee Mathews April 2016) (Citation: Sean Gallagher April 2016) (Citation: Dark Reading Staff April 2016) The plant has since checked for infection and cleaned up more than 1,000 computers. (Citation: BBC April 2016) An ESET researcher commented that internet disconnection does not guarantee system safety from infection or payload execution. (Citation: ESET April 2016) | https://attack.mitre.org/techniques/T0847 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Initial Access |  | None | Drive: Drive Creation, File: File Access, File: File Creation, Process: Process Creation |  | (Citation: Langer Stuxnet),(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Symantec June 2015),(Citation: Catalin Cimpanu April 2016),,
T0848 | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | Rogue Master | Adversaries may setup a rogue master to leverage control server functions to communicate with outstations. A rogue master can be used to send legitimate control messages to other control system devices, affecting processes in unintended ways. It may also be used to disrupt network communications by capturing and receiving the network traffic meant for the actual master. Impersonating a master may also allow an adversary to avoid detection. In the case of the 2017 Dallas Siren incident, adversaries used a rogue master to send command messages to the 156 distributed sirens across the city, either through a single rogue transmitter with a strong signal, or using many distributed repeaters. (Citation: Bastille April 2017) (Citation: Zack Whittaker April 2017) | https://attack.mitre.org/techniques/T0848 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Initial Access |  | None | Application Log: Application Log Content, Asset: Asset Inventory, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Device Alarm |  | (Citation: Marshall Abrams July 2008),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Dwight Anderson 2014),(Citation: Keith Stouffer May 2015),(Citation: Department of Homeland Security September 2016),
T0851 | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | Rootkit | Adversaries may deploy rootkits to hide the presence of programs, files, network connections, services, drivers, and other system components. Rootkits are programs that hide the existence of malware by intercepting and modifying operating-system API calls that supply system information. Rootkits or rootkit-enabling functionality may reside at the user or kernel level in the operating system, or lower. (Citation: Enterprise ATT&CK January 2018) Firmware rootkits that affect the operating system yield nearly full control of the system. While firmware rootkits are normally developed for the main processing board, they can also be developed for the I/O that is attached to an asset. Compromise of this firmware allows the modification of all of the process variables and functions the module engages in. This may result in commands being disregarded and false information being fed to the main device. By tampering with device processes, an adversary may inhibit its expected response functions and possibly enable [Impact](https://attack.mitre.org/tactics/TA0105). | https://attack.mitre.org/techniques/T0851 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Evasion, Inhibit Response Function |  | None | Firmware: Firmware Modification |  | (Citation: Langer Stuxnet),(Citation: IEC February 2019),
T0852 | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | Screen Capture | Adversaries may attempt to perform screen capture of devices in the control system environment. Screenshots may be taken of workstations, HMIs, or other devices that display environment-relevant process, device, reporting, alarm, or related data. These device displays may reveal information regarding the ICS process, layout, control, and related schematics. In particular, an HMI can provide a lot of important industrial process information. (Citation: ICS-CERT October 2017) Analysis of screen captures may provide the adversary with an understanding of intended operations and interactions between critical devices. | https://attack.mitre.org/techniques/T0852 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Collection |  | None | Command: Command Execution, Process: OS API Execution |  | (Citation: Jacqueline O'Leary et al. September 2017),(Citation: Junnosuke Yagi March 2017),(Citation: ICS-CERT October 2017),(Citation: Dragos),,
T0853 | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | Scripting | Adversaries may use scripting languages to execute arbitrary code in the form of a pre-written script or in the form of user-supplied code to an interpreter. Scripting languages are programming languages that differ from compiled languages, in that scripting languages use an interpreter, instead of a compiler. These interpreters read and compile part of the source code just before it is executed, as opposed to compilers, which compile each and every line of code to an executable file. Scripting allows software developers to run their code on any system where the interpreter exists. This way, they can distribute one package, instead of precompiling executables for many different systems. Scripting languages, such as Python, have their interpreters shipped as a default with many Linux distributions. In addition to being a useful tool for developers and administrators, scripting language interpreters may be abused by the adversary to execute code in the target environment. Due to the nature of scripting languages, this allows for weaponized code to be deployed to a target easily, and leaves open the possibility of on-the-fly scripting to perform a task. | https://attack.mitre.org/techniques/T0853 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Execution |  | None | Command: Command Execution, Module: Module Load, Process: Process Creation, Process: Process Metadata, Script: Script Execution |  | (Citation: Tom Fakterman August 2019),(Citation: DHS CISA February 2019),(Citation: FireEye TEMP.Veles 2018),(Citation: Dragos),(Citation: Mandiant-Sandworm-Ukraine-2022),(Citation: Symantec March 2019),(Citation: Dragos Crashoverride 2018),(Citation: Robert Falcone, Bryan Lee May 2016),,
T0881 | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | Service Stop | Adversaries may stop or disable services on a system to render those services unavailable to legitimate users. Stopping critical services can inhibit or stop response to an incident or aid in the adversary's overall objectives to cause damage to the environment. (Citation: Enterprise ATT&CK) Services may not allow for modification of their data stores while running. Adversaries may stop services in order to conduct Data Destruction. (Citation: Enterprise ATT&CK) | https://attack.mitre.org/techniques/T0881 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function |  | None | Command: Command Execution, File: File Modification, Process: OS API Execution, Process: Process Creation, Process: Process Termination, Service: Service Metadata, Windows Registry: Windows Registry Key Modification |  | (Citation: Industroyer2 Mandiant April 2022),(Citation: McAfee Labs October 2019),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020),(Citation: Anton Cherepanov),(Citation: Ben Hunter and Fred Gutierrez July 2020),(Citation: Department of Homeland Security September 2016),
T0865 | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | Spearphishing Attachment | Adversaries may use a spearphishing attachment, a variant of spearphishing, as a form of a social engineering attack against specific targets. Spearphishing attachments are different from other forms of spearphishing in that they employ malware attached to an email. All forms of spearphishing are electronically delivered and target a specific individual, company, or industry. In this scenario, adversaries attach a file to the spearphishing email and usually rely upon [User Execution](https://attack.mitre.org/techniques/T0863) to gain execution and access. (Citation: Enterprise ATT&CK October 2019) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012, targeted ONG organizations and their employees. The emails were constructed with a high level of sophistication to convince employees to open the malicious file attachments. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/techniques/T0865 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Initial Access |  | None | Application Log: Application Log Content, File: File Creation, Network Traffic: Network Traffic Content, Process: Process Creation |  | (Citation: Jacqueline O'Leary et al. September 2017),(Citation: Andy Greenburg June 2019),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Booz Allen Hamilton),(Citation: Robert Falcone, Bryan Lee May 2016),(Citation: Jeff Jones May 2018),(Citation: Eduard Kovacs March 2018),(Citation: Novetta Threat Research Group February 2016),,
T0856 | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | Spoof Reporting Message | Adversaries may spoof reporting messages in control system environments for evasion and to impair process control. In control systems, reporting messages contain telemetry data (e.g., I/O values) pertaining to the current state of equipment and the industrial process. Reporting messages are important for monitoring the normal operation of a system or identifying important events such as deviations from expected values. If an adversary has the ability to Spoof Reporting Messages, they can impact the control system in many ways. The adversary can Spoof Reporting Messages that state that the process is operating normally, as a form of evasion. The adversary could also Spoof Reporting Messages to make the defenders and operators think that other errors are occurring in order to distract them from the actual source of a problem. (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) | https://attack.mitre.org/techniques/T0856 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Evasion, Impair Process Control |  | None | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Device Alarm, Windows Registry: Windows Registry Key Modification |  | (Citation: Marshall Abrams July 2008),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Dwight Anderson 2014),(Citation: Keith Stouffer May 2015),(Citation: Department of Homeland Security September 2016),
T0869 | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | Standard Application Layer Protocol | Adversaries may establish command and control capabilities over commonly used application layer protocols such as HTTP(S), OPC, RDP, telnet, DNP3, and modbus. These protocols may be used to disguise adversary actions as benign network traffic. Standard protocols may be seen on their associated port or in some cases over a non-standard port. Adversaries may use these protocols to reach out of the network for command and control, or in some cases to other infected devices within the network. | https://attack.mitre.org/techniques/T0869 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Command and Control |  | None | Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Tom Fakterman August 2019),(Citation: Booz Allen Hamilton),(Citation: CISA-AA22-103A),(Citation: Jos Wetzels January 2018),(Citation: Robert Falcone, Bryan Lee May 2016),(Citation: SecureWorks September 2019),,
T0862 | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | Supply Chain Compromise | Adversaries may perform supply chain compromise to gain control systems environment access by means of infected products, software, and workflows. Supply chain compromise is the manipulation of products, such as devices or software, or their delivery mechanisms before receipt by the end consumer. Adversary compromise of these products and mechanisms is done for the goal of data or system compromise, once infected products are introduced to the target environment. Supply chain compromise can occur at all stages of the supply chain, from manipulation of development tools and environments to manipulation of developed products and tools distribution mechanisms. This may involve the compromise and replacement of legitimate software and patches, such as on third party or vendor websites. Targeting of supply chain compromise can be done in attempts to infiltrate the environments of a specific audience. In control systems environments with assets in both the IT and OT networks, it is possible a supply chain compromise affecting the IT environment could enable further access to the OT environment. Counterfeit devices may be introduced to the global supply chain posing safety and cyber risks to asset owners and operators. These devices may not meet the safety, engineering and manufacturing requirements of regulatory bodies but may feature tagging indicating conformance with industry standards. Due to the lack of adherence to standards and overall lesser quality, the counterfeit products may pose a serious safety and operational risk. (Citation: Control Global May 2019) Yokogawa identified instances in which their customers received counterfeit differential pressure transmitters using the Yokogawa logo. The counterfeit transmitters were nearly indistinguishable with a semblance of functionality and interface that mimics the genuine product. (Citation: Control Global May 2019) F-Secure Labs analyzed the approach the adversary used to compromise victim systems with Havex. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) The adversary planted trojanized software installers available on legitimate ICS/SCADA vendor websites. After being downloaded, this software infected the host computer with a Remote Access Trojan (RAT). | https://attack.mitre.org/techniques/T0862 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Initial Access |  | None | File: File Metadata |  | (Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Symantec Security Response July 2014),(Citation: Dragos Threat Intelligence August 2019),(Citation: Robert A. Martin January 2021),(Citation: OWASP),
T0894 | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | System Binary Proxy Execution | Adversaries may bypass process and/or signature-based defenses by proxying execution of malicious content with signed, or otherwise trusted, binaries. Binaries used in this technique are often Microsoft-signed files, indicating that they have been either downloaded from Microsoft or are already native in the operating system. (Citation: LOLBAS Project) Binaries signed with trusted digital certificates can typically execute on Windows systems protected by digital signature validation. Several Microsoft signed binaries that are default on Windows installations can be used to proxy execution of other files or commands. Similarly, on Linux systems adversaries may abuse trusted binaries such as split to proxy execution of malicious commands. (Citation: split man page)(Citation: GTFO split) Adversaries may abuse application binaries installed on a system for proxy execution of malicious code or domain-specific commands. These commands could be used to target local resources on the device or networked devices within the environment through defined APIs ([Execution through API](https://attack.mitre.org/techniques/T0871)) or application-specific programming languages (e.g., MicroSCADA SCIL). Application binaries may be signed by the developer or generally trusted by the operators, analysts, and monitoring tools accustomed to the environment. These applications may be developed and/or directly provided by the device vendor to enable configuration, management, and operation of their devices without many alternatives. Adversaries may seek to target these trusted application binaries to execute or send commands without the development of custom malware. For example, adversaries may target a SCADA server binary which has the existing ability to send commands to substation devices, such as through IEC 104 command messages. Proxy execution may still require the development of custom tools to hook into the application binary’s execution. | https://attack.mitre.org/techniques/T0894 | 25 March 2024 | 08 April 2024 | ics-attack | 1.0 | Evasion |  | None | Command: Command Execution, Process: Process Creation, Script: Script Execution |  | (Citation: Mandiant-Sandworm-Ukraine-2022),,
T0857 | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | System Firmware | System firmware on modern assets is often designed with an update feature. Older device firmware may be factory installed and require special reprograming equipment. When available, the firmware update feature enables vendors to remotely patch bugs and perform upgrades. Device firmware updates are often delegated to the user and may be done using a software update package. It may also be possible to perform this task over the network. An adversary may exploit the firmware update feature on accessible devices to upload malicious or out-of-date firmware. Malicious modification of device firmware may provide an adversary with root access to a device, given firmware is one of the lowest programming abstraction layers. (Citation: Basnight, Zachry, et al.) | https://attack.mitre.org/techniques/T0857 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Inhibit Response Function, Persistence |  | None | Application Log: Application Log Content, Firmware: Firmware Modification, Network Traffic: Network Traffic Content, Operational Databases: Device Alarm |  | (Citation: Ukraine15 - EISAC - 201603),(Citation: DHS CISA February 2019),(Citation: Intel),(Citation: N/A),(Citation: ESET Research Whitepapers September 2018),(Citation: Department of Homeland Security September 2016),
T0882 | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | Theft of Operational Information | Adversaries may steal operational information on a production environment as a direct mission outcome for personal gain or to inform future operations. This information may include design documents, schedules, rotational data, or similar artifacts that provide insight on operations. In the Bowman Dam incident, adversaries probed systems for operational data. (Citation: Mark Thompson March 2016) (Citation: Danny Yadron December 2015) | https://attack.mitre.org/techniques/T0882 | 21 May 2020 | 13 October 2023 | ics-attack | 1.0 | Impact |  | None |  |  | (Citation: McAfee Labs October 2019),(Citation: SecureWorks September 2019),(Citation: Symantec),(Citation: Kevin Savage and Branko Spasojevic),(Citation: ESET),(Citation: Keith Stouffer May 2015),(Citation: National Institute of Standards and Technology April 2013),
T0864 | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | Transient Cyber Asset | Adversaries may target devices that are transient across ICS networks and external networks. Normally, transient assets are brought into an environment by authorized personnel and do not remain in that environment on a permanent basis. (Citation: North American Electric Reliability Corporation June 2021) Transient assets are commonly needed to support management functions and may be more common in systems where a remotely managed asset is not feasible, external connections for remote access do not exist, or 3rd party contractor/vendor access is required. Adversaries may take advantage of transient assets in different ways. For instance, adversaries may target a transient asset when it is connected to an external network and then leverage its trusted access in another environment to launch an attack. They may also take advantage of installed applications and libraries that are used by legitimate end-users to interact with control system devices. Transient assets, in some cases, may not be deployed with a secure configuration leading to weaknesses that could allow an adversary to propagate malicious executable code, e.g., the transient asset may be infected by malware and when connected to an ICS environment the malware propagates onto other systems. | https://attack.mitre.org/techniques/T0864 | 14 October 2021 | 13 October 2023 | ics-attack | 1.2 | Initial Access |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Flow |  | (Citation: Marshall Abrams July 2008),(Citation: National Institute of Standards and Technology April 2013),(Citation: Emerson Exchange),(Citation: National Security Agency February 2016),(Citation: North America Transmission Forum December 2019),
T0855 | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | Unauthorized Command Message | Adversaries may send unauthorized command messages to instruct control system assets to perform actions outside of their intended functionality, or without the logical preconditions to trigger their expected function. Command messages are used in ICS networks to give direct instructions to control systems devices. If an adversary can send an unauthorized command message to a control system, then it can instruct the control systems device to perform an action outside the normal bounds of the device's actions. An adversary could potentially instruct a control systems device to perform an action that will cause an [Impact](https://attack.mitre.org/tactics/TA0105). (Citation: Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011) In the Dallas Siren incident, adversaries were able to send command messages to activate tornado alarm systems across the city without an impending tornado or other disaster. (Citation: Zack Whittaker April 2017) (Citation: Benjamin Freed March 2019) | https://attack.mitre.org/techniques/T0855 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Impair Process Control |  | None | Application Log: Application Log Content, Network Traffic: Network Traffic Content, Network Traffic: Network Traffic Flow, Operational Databases: Process History/Live Data, Operational Databases: Process/Event Alarm |  | (Citation: Industroyer2 Mandiant April 2022),(Citation: Anton Cherepanov, ESET June 2017),(Citation: CISA-AA22-103A),(Citation: Mandiant-Sandworm-Ukraine-2022),(Citation: Industroyer2 Forescout July 2022),(Citation: FireEye TRITON 2018),(Citation: Ukraine15 - EISAC - 201603),(Citation: Marshall Abrams July 2008),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Dwight Anderson 2014),(Citation: Keith Stouffer May 2015),(Citation: Department of Homeland Security September 2016),
T0863 | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | User Execution | Adversaries may rely on a targeted organizations user interaction for the execution of malicious code. User interaction may consist of installing applications, opening email attachments, or granting higher permissions to documents. Adversaries may embed malicious code or visual basic code into files such as Microsoft Word and Excel documents or software installers. (Citation: Booz Allen Hamilton) Execution of this code requires that the user enable scripting or write access within the document. Embedded code may not always be noticeable to the user especially in cases of trojanized software. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) A Chinese spearphishing campaign running from December 9, 2011 through February 29, 2012 delivered malware through spearphishing attachments which required user action to achieve execution. (Citation: CISA AA21-201A Pipeline Intrusion July 2021) | https://attack.mitre.org/techniques/T0863 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Execution |  | None | Application Log: Application Log Content, Command: Command Execution, File: File Access, Network Traffic: Network Connection Creation, Network Traffic: Network Traffic Content, Process: Process Creation |  | (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Tom Fakterman August 2019),(Citation: Kyle Wilhoit),(Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017),,
T0859 | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | Valid Accounts | Adversaries may steal the credentials of a specific user or service account using credential access techniques. In some cases, default credentials for control system devices may be publicly available. Compromised credentials may be used to bypass access controls placed on various resources on hosts and within the network, and may even be used for persistent access to remote systems. Compromised and default credentials may also grant an adversary increased privilege to specific systems and devices or access to restricted areas of the network. Adversaries may choose not to use malware or tools, in conjunction with the legitimate access those credentials provide, to make it harder to detect their presence or to control devices and send legitimate commands in an unintended way. Adversaries may also create accounts, sometimes using predefined account names and passwords, to provide a means of backup access for persistence. (Citation: Booz Allen Hamilton) The overlap of credentials and permissions across a network of systems is of concern because the adversary may be able to pivot across accounts and systems to reach a high level of access (i.e., domain or enterprise administrator) and possibly between the enterprise and operational technology environments. Adversaries may be able to leverage valid credentials from one system to gain access to another system. | https://attack.mitre.org/techniques/T0859 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Lateral Movement, Persistence |  | None | Logon Session: Logon Session Creation, Logon Session: Logon Session Metadata, User Account: User Account Authentication |  | (Citation: Booz Allen Hamilton),(Citation: Dragos),(Citation: CISA-AA22-103A),(Citation: Dragos Crashoverride 2018),(Citation: FireEye TRITON 2018),(Citation: Wylie-22),(Citation: Ukraine15 - EISAC - 201603),(Citation: Microsoft August 2018),(Citation: CISA June 2013),(Citation: Schweitzer Engineering Laboratories August 2015),(Citation: Microsoft February 2019),(Citation: Keith Stouffer May 2015),(Citation: Microsoft May 2017),
T0860 | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | Wireless Compromise | Adversaries may perform wireless compromise as a method of gaining communications and unauthorized access to a wireless network. Access to a wireless network may be gained through the compromise of a wireless device. (Citation: Alexander Bolshev, Gleb Cherbov July 2014) (Citation: Alexander Bolshev March 2014) Adversaries may also utilize radios and other wireless communication devices on the same frequency as the wireless network. Wireless compromise can be done as an initial access vector from a remote distance. A Polish student used a modified TV remote controller to gain access to and control over the Lodz city tram system in Poland. (Citation: John Bill May 2017) (Citation: Shelley Smith February 2008) The remote controller device allowed the student to interface with the trams network to modify track settings and override operator control. The adversary may have accomplished this by aligning the controller to the frequency and amplitude of IR control protocol signals. (Citation: Bruce Schneier January 2008) The controller then enabled initial access to the network, allowing the capture and replay of tram signals. (Citation: John Bill May 2017) | https://attack.mitre.org/techniques/T0860 | 21 May 2020 | 13 October 2023 | ics-attack | 1.2 | Initial Access |  | None | Application Log: Application Log Content, Logon Session: Logon Session Creation, Network Traffic: Network Traffic Flow | Scott Dougherty | (Citation: Marshall Abrams July 2008),(Citation: DHS National Urban Security Technology Laboratory April 2019),(Citation: CISA March 2010),
T0887 | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | Wireless Sniffing | Adversaries may seek to capture radio frequency (RF) communication used for remote control and reporting in distributed environments. RF communication frequencies vary between 3 kHz to 300 GHz, although are commonly between 300 MHz to 6 GHz. (Citation: Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. April 2018) The wavelength and frequency of the signal affect how the signal propagates through open air, obstacles (e.g. walls and trees) and the type of radio required to capture them. These characteristics are often standardized in the protocol and hardware and may have an effect on how the signal is captured. Some examples of wireless protocols that may be found in cyber-physical environments are: WirelessHART, Zigbee, WIA-FA, and 700 MHz Public Safety Spectrum. Adversaries may capture RF communications by using specialized hardware, such as software defined radio (SDR), handheld radio, or a computer with radio demodulator tuned to the communication frequency. (Citation: Bastille April 2017) Information transmitted over a wireless medium may be captured in-transit whether the sniffing device is the intended destination or not. This technique may be particularly useful to an adversary when the communications are not encrypted. (Citation: Gallagher, S. April 2017) In the 2017 Dallas Siren incident, it is suspected that adversaries likely captured wireless command message broadcasts on a 700 MHz frequency during a regular test of the system. These messages were later replayed to trigger the alarm systems. (Citation: Gallagher, S. April 2017) | https://attack.mitre.org/techniques/T0887 | 21 May 2020 | 13 October 2023 | ics-attack | 1.1 | Collection, Discovery |  | None | Network Traffic: Network Traffic Flow | ICSCoE Japan | ,(Citation: Bastille April 2017),(Citation: DHS National Urban Security Technology Laboratory April 2019),

## tactics
ID | STIX ID | name | description | url | created | last modified | domain | version
TA0100 | x-mitre-tactic--b2a67b1e-913c-46f6-b219-048a90560bb9 | Collection | The adversary is trying to gather data of interest and domain knowledge on your ICS environment to inform their goal. Collection consists of techniques adversaries use to gather domain knowledge and obtain contextual feedback in an ICS environment. This tactic is often performed as part of [Discovery](https://attack.mitre.org/tactics/TA0102), to compile data on control systems and targets of interest that may be used to follow through on the adversary’s objective. Examples of these techniques include observing operation states, capturing screenshots, identifying unique device roles, and gathering system and diagram schematics. Collection of this data can play a key role in planning, executing, and even revising an ICS-targeted attack. Methods of collection depend on the categories of data being targeted, which can include protocol specific, device specific, and process specific configurations and functionality. Information collected may pertain to a combination of system, supervisory, device, and network related data, which conceptually fall under high, medium, and low levels of plan operations. For example, information repositories on plant data at a high level or device specific programs at a low level. Sensitive floor plans, vendor device manuals, and other references may also be at risk and exposed on the internet or otherwise publicly accessible. | https://attack.mitre.org/tactics/TA0100 | 17 October 2018 | 08 March 2023 | ics-attack | 1.0
TA0101 | x-mitre-tactic--97c8ff73-bd14-4b6c-ac32-3d91d2c41e3f | Command and Control | The adversary is trying to communicate with and control compromised systems, controllers, and platforms with access to your ICS environment. Command and Control consists of techniques that adversaries use to communicate with and send commands to compromised systems, devices, controllers, and platforms with specialized applications used in ICS environments. Examples of these specialized communication devices include human machine interfaces (HMIs), data historians, SCADA servers, and engineering workstations (EWS). Adversaries often seek to use commonly available resources and mimic expected network traffic to avoid detection and suspicion. For instance, commonly used ports and protocols in ICS environments, and even expected IT resources, depending on the target network. Command and Control may be established to varying degrees of stealth, often depending on the victim’s network structure and defenses. | https://attack.mitre.org/tactics/TA0101 | 17 October 2018 | 09 March 2023 | ics-attack | 1.0
TA0102 | x-mitre-tactic--696af733-728e-49d7-8261-75fdc590f453 | Discovery | The adversary is locating information to assess and identify their targets in your environment. Discovery consists of techniques that adversaries use to survey your ICS environment and gain knowledge about the internal network, control system devices, and how their processes interact. These techniques help adversaries observe the environment and determine next steps for target selection and Lateral Movement. They also allow adversaries to explore what they can control and gain insight on interactions between various control system processes. Discovery techniques are often an act of progression into the environment which enable the adversary to orient themselves before deciding how to act. Adversaries may use Discovery techniques that result in Collection, to help determine how available resources benefit their current objective. A combination of native device communications and functions, and custom tools are often used toward this post-compromise information-gathering objective. | https://attack.mitre.org/tactics/TA0102 | 17 October 2018 | 09 March 2023 | ics-attack | 1.0
TA0103 | x-mitre-tactic--ddf70682-f3ce-479c-a9a4-7eadf9bfead7 | Evasion | The adversary is trying to avoid security defenses. Evasion consists of techniques that adversaries use to avoid technical defenses throughout their campaign. Techniques used for evasion include removal of indicators of compromise, spoofing communications, and exploiting software vulnerabilities. Adversaries may also leverage and abuse trusted devices and processes to hide their activity, possibly by masquerading as master devices or native software. Methods of defense evasion for this purpose are often more passive in nature. | https://attack.mitre.org/tactics/TA0103 | 17 October 2018 | 09 March 2023 | ics-attack | 1.0
TA0104 | x-mitre-tactic--93bf9a8e-b14c-4587-b6d5-9efc7c12eb45 | Execution | The adversary is trying to run code or manipulate system functions, parameters, and data in an unauthorized way. Execution consists of techniques that result in adversary-controlled code running on a local or remote system, device, or other asset. This execution may also rely on unknowing end users or the manipulation of device operating modes to run. Adversaries may infect remote targets with programmed executables or malicious project files that operate according to specified behavior and may alter expected device behavior in subtle ways. Commands for execution may also be issued from command-line interfaces, APIs, GUIs, or other available interfaces. Techniques that run malicious code may also be paired with techniques from other tactics, particularly to aid network [Discovery](https://attack.mitre.org/tactics/TA0102) and [Collection](https://attack.mitre.org/tactics/TA0100), impact operations, and inhibit response functions. | https://attack.mitre.org/tactics/TA0104 | 17 October 2018 | 08 March 2023 | ics-attack | 1.0
TA0105 | x-mitre-tactic--77542f83-70d0-40c2-8a9d-ad2eb8b00279 | Impact | The adversary is trying to manipulate, interrupt, or destroy your ICS systems, data, and their surrounding environment. Impact consists of techniques that adversaries use to disrupt, compromise, destroy, and manipulate the integrity and availability of control system operations, processes, devices, and data. These techniques encompass the influence and effects resulting from adversarial efforts to attack the ICS environment or that tangentially impact it. Impact techniques can result in more instantaneous disruption to control processes and the operator, or may result in more long term damage or loss to the ICS environment and related operations. The adversary may leverage [Impair Process Control](https://attack.mitre.org/tactics/TA0106) techniques, which often manifest in more self-revealing impacts on operations, or [Impair Process Control](https://attack.mitre.org/tactics/TA0106) techniques to hinder safeguards and alarms in order to follow through with and provide cover for Impact. In some scenarios, control system processes can appear to function as expected, but may have been altered to benefit the adversary’s goal over the course of a longer duration. These techniques might be used by adversaries to follow through on their end goal or to provide cover for a confidentiality breach. [Loss of Productivity and Revenue](https://attack.mitre.org/techniques/T0828), [Theft of Operational Information](https://attack.mitre.org/techniques/T0882), and [Damage to Property](https://attack.mitre.org/techniques/T0879) are meant to encompass some of the more granular goals of adversaries in targeted and untargeted attacks. These techniques in and of themselves are not necessarily detectable, but the associated adversary behavior can potentially be mitigated and/or detected. | https://attack.mitre.org/tactics/TA0105 | 14 March 2019 | 08 March 2023 | ics-attack | 1.0
TA0106 | x-mitre-tactic--ff048b6c-b872-4218-b68c-3735ebd1f024 | Impair Process Control | The adversary is trying to manipulate, disable, or damage physical control processes. Impair Process Control consists of techniques that adversaries use to disrupt control logic and cause determinantal effects to processes being controlled in the target environment. Targets of interest may include active procedures or parameters that manipulate the physical environment. These techniques can also include prevention or manipulation of reporting elements and control logic. If an adversary has modified process functionality, then they may also obfuscate the results, which are often self-revealing in their impact on the outcome of a product or the environment. The direct physical control these techniques exert may also threaten the safety of operators and downstream users, which can prompt response mechanisms. Adversaries may follow up with or use [Inhibit Response Function](https://attack.mitre.org/tactics/TA0107) techniques in tandem, to assist with the successful abuse of control processes to result in [Impact](https://attack.mitre.org/tactics/TA0105). | https://attack.mitre.org/tactics/TA0106 | 17 October 2018 | 08 March 2023 | ics-attack | 1.0
TA0107 | x-mitre-tactic--298fe907-7931-4fd2-8131-2814dd493134 | Inhibit Response Function | The adversary is trying to prevent your safety, protection, quality assurance, and operator intervention functions from responding to a failure, hazard, or unsafe state. Inhibit Response Function consists of techniques that adversaries use to hinder the safeguards put in place for processes and products. This may involve the inhibition of safety, protection, quality assurance, or operator intervention functions to disrupt safeguards that aim to prevent the loss of life, destruction of equipment, and disruption of production. These techniques aim to actively deter and prevent expected alarms and responses that arise due to statuses in the ICS environment. Adversaries may modify or update system logic, or even outright prevent responses with a denial-of-service. They may result in the prevention, destruction, manipulation, or modification of programs, logic, devices, and communications. As prevention functions are generally dormant, reporting and processing functions can appear fine, but may have been altered to prevent failure responses in dangerous scenarios. Unlike [Evasion](https://attack.mitre.org/tactics/TA0103), Inhibit Response Function techniques may be more intrusive, such as actively preventing responses to a known dangerous scenario. Adversaries may use these techniques to follow through with or provide cover for [Impact](https://attack.mitre.org/tactics/TA0105) techniques. | https://attack.mitre.org/tactics/TA0107 | 17 October 2018 | 08 March 2023 | ics-attack | 1.0
TA0108 | x-mitre-tactic--69da72d2-f550-41c5-ab9e-e8255707f28a | Initial Access | The adversary is trying to get into your ICS environment. Initial Access consists of techniques that adversaries may use as entry vectors to gain an initial foothold within an ICS environment. These techniques include compromising operational technology assets, IT resources in the OT network, and external remote services and websites. They may also target third party entities and users with privileged access. In particular, these initial access footholds may include devices and communication mechanisms with access to and privileges in both the IT and OT environments. IT resources in the OT environment are also potentially vulnerable to the same attacks as enterprise IT systems. Trusted third parties of concern may include vendors, maintenance personnel, engineers, external integrators, and other outside entities involved in expected ICS operations. Vendor maintained assets may include physical devices, software, and operational equipment. Initial access techniques may also leverage outside devices, such as radios, controllers, or removable media, to remotely interfere with and possibly infect OT operations. | https://attack.mitre.org/tactics/TA0108 | 17 October 2018 | 09 March 2023 | ics-attack | 1.0
TA0109 | x-mitre-tactic--51c25a9e-8615-40c0-8afd-1da578847924 | Lateral Movement | The adversary is trying to move through your ICS environment. Lateral Movement consists of techniques that adversaries use to enter and control remote systems on a network. These techniques abuse default credentials, known accounts, and vulnerable services, and may also leverage dual-homed devices and systems that reside on both the IT and OT networks. The adversary uses these techniques to pivot to their next point in the environment, positioning themselves to where they want to be or think they should be. Following through on their primary objective often requires [Discovery](https://attack.mitre.org/tactics/TA0102) of the network and [Collection](https://attack.mitre.org/tactics/TA0100) to develop awareness of unique ICS devices and processes, in order to find their target and subsequently gain access to it. Reaching this objective often involves pivoting through multiple systems, devices, and accounts. Adversaries may install their own remote tools to accomplish Lateral Movement or leverage default tools, programs, and manufacturer set or other legitimate credentials native to the network, which may be stealthier. | https://attack.mitre.org/tactics/TA0109 | 17 October 2018 | 08 March 2023 | ics-attack | 1.0
TA0110 | x-mitre-tactic--78f1d2ae-a579-44c4-8fc5-3e1775c73fac | Persistence | The adversary is trying to maintain their foothold in your ICS environment. Persistence consists of techniques that adversaries use to maintain access to ICS systems and devices across restarts, changed credentials, and other interruptions that could cut off their access. Techniques used for persistence include any access, action, or configuration changes that allow them to secure their ongoing activity and keep their foothold on systems. This may include replacing or hijacking legitimate code, firmware, and other project files, or adding startup code and downloading programs onto devices. | https://attack.mitre.org/tactics/TA0110 | 17 October 2018 | 09 March 2023 | ics-attack | 1.0
TA0111 | x-mitre-tactic--33752ae7-f875-4f43-bdb6-d8d02d341046 | Privilege Escalation | The adversary is trying to gain higher-level permissions. Privilege Escalation consists of techniques that adversaries use to gain higher-level permissions on a system or network. Adversaries can often enter and explore a network with unprivileged access but require elevated permissions to follow through on their objectives. Common approaches are to take advantage of system weaknesses, misconfigurations, and vulnerabilities. | https://attack.mitre.org/tactics/TA0111 | 10 April 2021 | 29 September 2022 | ics-attack | 1.0

## software
ID | STIX ID | name | description | url | created | last modified | domain | version | platforms | aliases | type | contributors | relationship citations
S1000 | malware--a4a98eab-b691-45d9-8c48-869ef8fefd57 | ACAD/Medre.A | [ACAD/Medre.A](https://attack.mitre.org/software/S1000) is a worm that steals operational information. The worm collects AutoCAD files with drawings. [ACAD/Medre.A](https://attack.mitre.org/software/S1000) has the capability to be used for industrial espionage.(Citation: ESET) | https://attack.mitre.org/software/S1000 | 31 May 2017 | 12 October 2022 | ics-attack | 1.0 |  |  | malware |  | ,,(Citation: ESET)
S0093 | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | Backdoor.Oldrea | [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) is a modular backdoor that used by [Dragonfly](https://attack.mitre.org/groups/G0035) against energy companies since at least 2013. [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) was distributed via supply chain compromise, and included specialized modules to enumerate and map ICS-specific systems, processes, and protocols.(Citation: Symantec Dragonfly)(Citation: Gigamon Berserk Bear October 2021)(Citation: Symantec Dragonfly Sept 2017) | https://attack.mitre.org/software/S0093 | 31 May 2017 | 12 October 2022 | enterprise-attack,ics-attack | 2.0 | Windows | Havex | malware |  | (Citation: Symantec Dragonfly),(Citation: Gigamon Berserk Bear October 2021),,(Citation: Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell December 2015),(Citation: ICS-CERT August 2018),(Citation: Daavid Hentunen, Antti Tikkanen June 2014),(Citation: Kyle Wilhoit)
S0606 | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | Bad Rabbit | [Bad Rabbit](https://attack.mitre.org/software/S0606) is a self-propagating ransomware that affected the Ukrainian transportation sector in 2017. [Bad Rabbit](https://attack.mitre.org/software/S0606) has also targeted organizations and consumers in Russia. (Citation: Secure List Bad Rabbit)(Citation: ESET Bad Rabbit)(Citation: Dragos IT ICS Ransomware) | https://attack.mitre.org/software/S0606 | 09 February 2021 | 12 October 2022 | enterprise-attack,ics-attack | 1.0 | Windows | Win32/Diskcoder.D | malware |  | (Citation: Secureworks IRON VIKING ),,(Citation: Marc-Etienne M.Lveill October 2017),(Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017),(Citation: Joe Slowik April 2019)
S0089 | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | BlackEnergy | [BlackEnergy](https://attack.mitre.org/software/S0089) is a malware toolkit that has been used by both criminal and APT actors. It dates back to at least 2007 and was originally designed to create botnets for use in conducting Distributed Denial of Service (DDoS) attacks, but its use has evolved to support various plug-ins. It is well known for being used during the confrontation between Georgia and Russia in 2008, as well as in targeting Ukrainian institutions. Variants include BlackEnergy 2 and BlackEnergy 3. (Citation: F-Secure BlackEnergy 2014) | https://attack.mitre.org/software/S0089 | 31 May 2017 | 06 October 2023 | enterprise-attack,ics-attack | 1.4 | Windows | Black Energy | malware |  | (Citation: UK NCSC Olympic Attacks October 2020),(Citation: iSIGHT Sandworm 2014),(Citation: US District Court Indictment GRU Unit 74455 October 2020),(Citation: F-Secure BlackEnergy 2014),(Citation: Secureworks IRON VIKING ),(Citation: Booz Allen Hamilton),(Citation: Booz Allen Hamilton)
S0608 | malware--58eddbaf-7416-419a-ad7b-e65b9d4c3b55 | Conficker | [Conficker](https://attack.mitre.org/software/S0608) is a computer worm first detected in October 2008 that targeted Microsoft Windows using the MS08-067 Windows vulnerability to spread.(Citation: SANS Conficker) In 2016, a variant of [Conficker](https://attack.mitre.org/software/S0608) made its way on computers and removable disk drives belonging to a nuclear power plant.(Citation: Conficker Nuclear Power Plant) | https://attack.mitre.org/software/S0608 | 23 February 2021 | 08 March 2023 | enterprise-attack,ics-attack | 1.0 | Windows | Downadup, Kido | malware |  | ,,(Citation: Symantec June 2015),(Citation: Catalin Cimpanu April 2016)
S0038 | malware--68dca94f-c11d-421e-9287-7c501108e18c | Duqu | [Duqu](https://attack.mitre.org/software/S0038) is a malware platform that uses a modular approach to extend functionality after deployment within a target network. (Citation: Symantec W32.Duqu) | https://attack.mitre.org/software/S0038 | 31 May 2017 | 08 March 2023 | enterprise-attack,ics-attack | 1.2 | Windows |  | malware |  | ,,(Citation: Symantec)
S0605 | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | EKANS | [EKANS](https://attack.mitre.org/software/S0605) is ransomware variant written in Golang that first appeared in mid-December 2019 and has been used against multiple sectors, including energy, healthcare, and automotive manufacturing, which in some cases resulted in significant operational disruptions. [EKANS](https://attack.mitre.org/software/S0605) has used a hard-coded kill-list of processes, including some associated with common ICS software platforms (e.g., GE Proficy, Honeywell HMIWeb, etc), similar to those defined in [MegaCortex](https://attack.mitre.org/software/S0576).(Citation: Dragos EKANS)(Citation: Palo Alto Unit 42 EKANS) | https://attack.mitre.org/software/S0605 | 12 February 2021 | 08 March 2023 | enterprise-attack,ics-attack | 2.0 | Windows | SNAKEHOSE | malware |  | ,,(Citation: Davey Winder June 2020),(Citation: Ben Hunter and Fred Gutierrez July 2020),(Citation: Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020),(Citation: Dragos Threat Intelligence February 2020)
S0143 | malware--ff6840c9-4c87-4d07-bbb6-9f50aa33d498 | Flame | [Flame](https://attack.mitre.org/software/S0143) is a sophisticated toolkit that has been used to collect information since at least 2010, largely targeting Middle East countries. (Citation: Kaspersky Flame) | https://attack.mitre.org/software/S0143 | 31 May 2017 | 12 October 2022 | enterprise-attack,ics-attack | 1.1 | Windows | Flamer, sKyWIper | malware |  | ,,(Citation: Kevin Savage and Branko Spasojevic)
S1045 | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | INCONTROLLER | [INCONTROLLER](https://attack.mitre.org/software/S1045) is custom malware that includes multiple modules tailored towards ICS devices and technologies, including Schneider Electric and Omron PLCs as well as OPC UA, Modbus, and CODESYS protocols. [INCONTROLLER](https://attack.mitre.org/software/S1045) has the ability to discover specific devices, download logic on the devices, and exploit platform-specific vulnerabilities. As of September 2022, some security researchers assessed [INCONTROLLER](https://attack.mitre.org/software/S1045) was developed by CHERNOVITE.(Citation: CISA-AA22-103A)(Citation: Brubaker-Incontroller)(Citation: Dragos-Pipedream)(Citation: Schneider-Incontroller)(Citation: Wylie-22) | https://attack.mitre.org/software/S1045 | 28 September 2022 | 17 March 2023 | ics-attack | 1.0 | Engineering Workstation, Field Controller/RTU/PLC/IED, Safety Instrumented System/Protection Relay, Windows | PIPEDREAM | malware | Jimmy Wylie, Dragos, Inc. | ,,(Citation: Wylie-22),(Citation: Brubaker-Incontroller),(Citation: Dragos-Pipedream),(Citation: CISA-AA22-103A)
S0604 | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | Industroyer | [Industroyer](https://attack.mitre.org/software/S0604) is a sophisticated malware framework designed to cause an impact to the working processes of Industrial Control Systems (ICS), specifically components used in electrical substations.(Citation: ESET Industroyer) [Industroyer](https://attack.mitre.org/software/S0604) was used in the attacks on the Ukrainian power grid in December 2016.(Citation: Dragos Crashoverride 2017) This is the first publicly known malware specifically designed to target and impact operations in the electric grid.(Citation: Dragos Crashoverride 2018) | https://attack.mitre.org/software/S0604 | 04 January 2021 | 11 April 2024 | enterprise-attack,ics-attack | 1.1 | Windows | CRASHOVERRIDE, Win32/Industroyer | malware | Dragos Threat Intelligence; Joe Slowik - Dragos | (Citation: Dragos Crashoverride 2018),(Citation: Dragos Crashoverride 2017),(Citation: Secureworks IRON VIKING),(Citation: ESET Industroyer),(Citation: Dragos Crashoverride 2018),(Citation: ESET Industroyer),(Citation: Anton Cherepanov, ESET June 2017),(Citation: Dragos Inc. June 2017),(Citation: Joe Slowik August 2019),(Citation: ESET Industroyer)
S1072 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | Industroyer2 | [Industroyer2](https://attack.mitre.org/software/S1072) is a compiled and static piece of malware that has the ability to communicate over the IEC-104 protocol. It is similar to the IEC-104 module found in [Industroyer](https://attack.mitre.org/software/S0604). Security researchers assess that [Industroyer2](https://attack.mitre.org/software/S1072) was designed to cause impact to high-voltage electrical substations. The initial [Industroyer2](https://attack.mitre.org/software/S1072) sample was compiled on 03/23/2022 and scheduled to execute on 04/08/2022, however it was discovered before deploying, resulting in no impact.(Citation: Industroyer2 Blackhat ESET) | https://attack.mitre.org/software/S1072 | 30 March 2023 | 06 April 2023 | ics-attack,enterprise-attack | 1.0 | Engineering Workstation, Field Controller/RTU/PLC/IED |  | malware |  | (Citation: Industroyer2 ESET April 2022),,(Citation: Industroyer2 Mandiant April 2022),(Citation: Industroyer2 Forescout July 2022),(Citation: Industroyer2 ESET April 2022)
S0607 | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | KillDisk | [KillDisk](https://attack.mitre.org/software/S0607) is a disk-wiping tool designed to overwrite files with random data to render the OS unbootable. It was first observed as a component of [BlackEnergy](https://attack.mitre.org/software/S0089) malware during cyber attacks against Ukraine in 2015. [KillDisk](https://attack.mitre.org/software/S0607) has since evolved into stand-alone malware used by a variety of threat actors against additional targets in Europe and Latin America; in 2016 a ransomware component was also incorporated into some [KillDisk](https://attack.mitre.org/software/S0607) variants.(Citation: KillDisk Ransomware)(Citation: ESEST Black Energy Jan 2016)(Citation: Trend Micro KillDisk 1)(Citation: Trend Micro KillDisk 2) | https://attack.mitre.org/software/S0607 | 20 January 2021 | 06 October 2023 | enterprise-attack,ics-attack | 1.2 | Linux, Windows | Win32/KillDisk.NBB, Win32/KillDisk.NBC, Win32/KillDisk.NBD, Win32/KillDisk.NBH, Win32/KillDisk.NBI | malware |  | (Citation: US District Court Indictment GRU Unit 74455 October 2020),(Citation: ESET Lazarus KillDisk April 2018),(Citation: Secureworks IRON VIKING ),(Citation: Booz Allen Hamilton),(Citation: Anton Cherepanov),(Citation: Booz Allen Hamilton)
S0372 | malware--5af7a825-2d9f-400d-931a-e00eb9e27f48 | LockerGoga | [LockerGoga](https://attack.mitre.org/software/S0372) is ransomware that was first reported in January 2019, and has been tied to various attacks on European companies, including industrial and manufacturing firms.(Citation: Unit42 LockerGoga 2019)(Citation: CarbonBlack LockerGoga 2019) | https://attack.mitre.org/software/S0372 | 16 April 2019 | 17 October 2023 | enterprise-attack,ics-attack | 2.0 | Windows |  | malware | Joe Slowik - Dragos | (Citation: FireEye FIN6 Apr 2019),,(Citation: Kevin Beaumont),(Citation: Hydro)
S0368 | malware--5719af9d-6b16-46f9-9b28-fb019541ddbb | NotPetya | [NotPetya](https://attack.mitre.org/software/S0368) is malware that was used by [Sandworm Team](https://attack.mitre.org/groups/G0034) in a worldwide attack starting on June 27, 2017. While [NotPetya](https://attack.mitre.org/software/S0368) appears as a form of ransomware, its main purpose was to destroy data and disk structures on compromised systems; the attackers never intended to make the encrypted data recoverable. As such, [NotPetya](https://attack.mitre.org/software/S0368) may be more appropriately thought of as a form of wiper malware. [NotPetya](https://attack.mitre.org/software/S0368) contains worm-like features to spread itself across a computer network using the SMBv1 exploits EternalBlue and EternalRomance.(Citation: Talos Nyetya June 2017)(Citation: US-CERT NotPetya 2017)(Citation: ESET Telebots June 2017)(Citation: US District Court Indictment GRU Unit 74455 October 2020) | https://attack.mitre.org/software/S0368 | 26 March 2019 | 08 March 2023 | enterprise-attack,ics-attack | 2.0 | Windows | Diskcoder.C, ExPetr, GoldenEye, Nyetya, Petrwrap | malware |  | (Citation: NCSC Sandworm Feb 2020),(Citation: UK NCSC Olympic Attacks October 2020),(Citation: Trend Micro Cyclops Blink March 2022),(Citation: US District Court Indictment GRU Unit 74455 October 2020),(Citation: Secureworks IRON VIKING ),,(Citation: Joe Slowik April 2019),(Citation: David Voreacos, Katherine Chinglinsky, Riley Griffin December 2019)
S1006 | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | PLC-Blaster | [PLC-Blaster](https://attack.mitre.org/software/S1006) is a piece of proof-of-concept malware that runs on Siemens S7 PLCs. This worm locates other Siemens S7 PLCs on the network and attempts to infect them. Once this worm has infected its target and attempted to infect other devices on the network, the worm can then run one of many modules. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) (Citation: Spenneberg, Ralf 2016) | https://attack.mitre.org/software/S1006 | 26 March 2019 | 12 October 2022 | ics-attack | 1.0 |  |  | malware |  | ,,(Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016)
S0496 | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | REvil | [REvil](https://attack.mitre.org/software/S0496) is a ransomware family that has been linked to the [GOLD SOUTHFIELD](https://attack.mitre.org/groups/G0115) group and operated as ransomware-as-a-service (RaaS) since at least April 2019. [REvil](https://attack.mitre.org/software/S0496), which as been used against organizations in the manufacturing, transportation, and electric sectors, is highly configurable and shares code similarities with the GandCrab RaaS.(Citation: Secureworks REvil September 2019)(Citation: Intel 471 REvil March 2020)(Citation: Group IB Ransomware May 2020) | https://attack.mitre.org/software/S0496 | 04 August 2020 | 11 April 2024 | enterprise-attack,ics-attack | 2.2 | Windows | Sodin, Sodinokibi | malware | Edward Millington | (Citation: IBM Ransomware Trends September 2020),(Citation: CrowdStrike Carbon Spider August 2021),(Citation: Microsoft Ransomware as a Service),(Citation: FBI Flash FIN7 USB),(Citation: Secureworks GandCrab and REvil September 2019),(Citation: Secureworks REvil September 2019),,(Citation: McAfee Labs October 2019),(Citation: Tom Fakterman August 2019),(Citation: Max Heinemeyer February 2020),(Citation: SecureWorks September 2019),(Citation: Selena Larson, Camille Singleton December 2020)
S0446 | malware--a020a61c-423f-4195-8c46-ba1d21abba37 | Ryuk | [Ryuk](https://attack.mitre.org/software/S0446) is a ransomware designed to target enterprise environments that has been used in attacks since at least 2018. [Ryuk](https://attack.mitre.org/software/S0446) shares code similarities with Hermes ransomware.(Citation: CrowdStrike Ryuk January 2019)(Citation: FireEye Ryuk and Trickbot January 2019)(Citation: FireEye FIN6 Apr 2019) | https://attack.mitre.org/software/S0446 | 13 May 2020 | 09 August 2023 | enterprise-attack,ics-attack | 1.4 | Windows |  | malware | Matt Brenton, Zurich Insurance Group; The DFIR Report, @TheDFIRReport | (Citation: Mandiant FIN12 Oct 2021),(Citation: DFIR Ryuk 2 Hour Speed Run November 2020),(Citation: DFIR Ryuk in 5 Hours October 2020),(Citation: FireEye KEGTAP SINGLEMALT October 2020),(Citation: CrowdStrike Wizard Spider October 2020),(Citation: Microsoft Ransomware as a Service),(Citation: DFIR Ryuk's Return October 2020),(Citation: FireEye FIN6 Apr 2019),(Citation: CrowdStrike Ryuk January 2019),(Citation: Sophos New Ryuk Attack October 2020),(Citation: Red Canary Hospital Thwarted Ryuk October 2020),(Citation: DHS/CISA Ransomware Targeting Healthcare October 2020),,(Citation: Kelly Jackson Higgins)
S0603 | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | Stuxnet | [Stuxnet](https://attack.mitre.org/software/S0603) was the first publicly reported piece of malware to specifically target industrial control systems devices. [Stuxnet](https://attack.mitre.org/software/S0603) is a large and complex piece of malware that utilized multiple different behaviors including multiple zero-day vulnerabilities, a sophisticated Windows rootkit, and network infection routines.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011)(Citation: CISA ICS Advisory ICSA-10-272-01)(Citation: ESET Stuxnet Under the Microscope)(Citation: Langer Stuxnet) [Stuxnet](https://attack.mitre.org/software/S0603) was discovered in 2010, with some components being used as early as November 2008.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | https://attack.mitre.org/software/S0603 | 14 December 2020 | 10 April 2024 | enterprise-attack,ics-attack | 1.4 | Windows | W32.Stuxnet | malware |  | ,,(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011),(Citation: Langer Stuxnet)
S1009 | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | Triton | [Triton](https://attack.mitre.org/software/S1009) is an attack framework built to interact with Triconex Safety Instrumented System (SIS) controllers.(Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017)(Citation: Dragos December 2017)(Citation: DHS CISA February 2019)(Citation: Schneider Electric January 2018)(Citation: Julian Gutmanis March 2019)(Citation: Schneider December 2018)(Citation: Jos Wetzels January 2018) | https://attack.mitre.org/software/S1009 | 26 March 2019 | 17 April 2024 | ics-attack | 1.1 |  | HatMan, TRISIS | malware |  | (Citation: Dragos Xenotime 2018),(Citation: FireEye TRITON 2018),(Citation: FireEye TRITON Dec 2017),(Citation: FireEye TEMP.Veles 2018),(Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017),(Citation: DHS CISA February 2019),(Citation: Jos Wetzels January 2018),(Citation: The Office of Nuclear Reactor Regulation),(Citation: FireEye TRITON),(Citation: Schneider Electric January 2018),(Citation: MDudek-ICS),(Citation: ICS-CERT December 2018)
S1010 | malware--6108f800-10b8-4090-944e-be579f01263d | VPNFilter | [VPNFilter](https://attack.mitre.org/software/S1010) is a multi-stage, modular platform with versatile capabilities to support both intelligence-collection and destructive cyber attack operations. [VPNFilter](https://attack.mitre.org/software/S1010) modules such as its packet sniffer ('ps') can collect traffic that passes through an infected device, allowing the theft of website credentials and monitoring of Modbus SCADA protocols. (Citation: William Largent June 2018) (Citation: Carl Hurd March 2019) | https://attack.mitre.org/software/S1010 | 26 March 2019 | 07 March 2024 | ics-attack | 1.1 |  |  | malware |  | ,,(Citation: William Largent June 2018),(Citation: Carl Hurd March 2019)
S0366 | malware--75ecdbf1-c2bb-4afc-a3f9-c8da4de8c661 | WannaCry | [WannaCry](https://attack.mitre.org/software/S0366) is ransomware that was first seen in a global attack during May 2017, which affected more than 150 countries. It contains worm-like features to spread itself across a computer network using the SMBv1 exploit EternalBlue.(Citation: LogRhythm WannaCry)(Citation: US-CERT WannaCry 2017)(Citation: Washington Post WannaCry 2017)(Citation: FireEye WannaCry 2017) | https://attack.mitre.org/software/S0366 | 25 March 2019 | 08 March 2023 | enterprise-attack,ics-attack | 1.1 | Windows | WCry, WanaCry, WanaCrypt, WanaCrypt0r | malware | Jan Miller, CrowdStrike | (Citation: FireEye WannaCry 2017),(Citation: FireEye APT38 Oct 2018),(Citation: LogRhythm WannaCry),(Citation: SecureWorks WannaCry Analysis),,(Citation: Joe Slowik April 2019)

## groups
ID | STIX ID | name | description | url | created | last modified | domain | version | contributors | associated groups | associated groups citations | relationship citations
G1000 | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | ALLANITE | [ALLANITE](https://attack.mitre.org/groups/G1000) is a suspected Russian cyber espionage group, that has primarily targeted the electric utility sector within the United States and United Kingdom. The group's tactics and techniques are reportedly similar to [Dragonfly](https://attack.mitre.org/groups/G0035), although [ALLANITE](https://attack.mitre.org/groups/G1000)s technical capabilities have not exhibited disruptive or destructive abilities. It has been suggested that the group maintains a presence in ICS for the purpose of gaining understanding of processes and to maintain persistence. (Citation: Dragos) | https://attack.mitre.org/groups/G1000 | 31 May 2017 | 24 May 2022 | ics-attack | 1.0 | Dragos Threat Intelligence | Palmetto Fusion |  | ,(Citation: Jeff Jones May 2018),(Citation: Eduard Kovacs May 2018),(Citation: ICS-CERT October 2017),(Citation: Dragos),
G0064 | intrusion-set--fbd29c89-18ba-4c2d-b792-51c0adee049f | APT33 | [APT33](https://attack.mitre.org/groups/G0064) is a suspected Iranian threat group that has carried out operations since at least 2013. The group has targeted organizations across multiple industries in the United States, Saudi Arabia, and South Korea, with a particular interest in the aviation and energy sectors.(Citation: FireEye APT33 Sept 2017)(Citation: FireEye APT33 Webinar Sept 2017) | https://attack.mitre.org/groups/G0064 | 18 April 2018 | 11 April 2024 | ics-attack,enterprise-attack | 2.0 | Dragos Threat Intelligence | Elfin, HOLMIUM, Peach Sandstorm | (Citation: Symantec Elfin Mar 2019), (Citation: Microsoft Holmium June 2020), (Citation: Microsoft Threat Actor Naming July 2023) | ,(Citation: Jacqueline O'Leary et al. September 2017),(Citation: Dragos),(Citation: Symantec March 2019),(Citation: Junnosuke Yagi March 2017),(Citation: Andy Greenburg June 2019),
G0082 | intrusion-set--00f67a77-86a4-4adf-be26-1a54fc713340 | APT38 | [APT38](https://attack.mitre.org/groups/G0082) is a North Korean state-sponsored threat group that specializes in financial cyber operations; it has been attributed to the Reconnaissance General Bureau.(Citation: CISA AA20-239A BeagleBoyz August 2020) Active since at least 2014, [APT38](https://attack.mitre.org/groups/G0082) has targeted banks, financial institutions, casinos, cryptocurrency exchanges, SWIFT system endpoints, and ATMs in at least 38 countries worldwide. Significant operations include the 2016 Bank of Bangladesh heist, during which [APT38](https://attack.mitre.org/groups/G0082) stole $81 million, as well as attacks against Bancomext (Citation: FireEye APT38 Oct 2018) and Banco de Chile (Citation: FireEye APT38 Oct 2018); some of their attacks have been destructive.(Citation: CISA AA20-239A BeagleBoyz August 2020)(Citation: FireEye APT38 Oct 2018)(Citation: DOJ North Korea Indictment Feb 2021)(Citation: Kaspersky Lazarus Under The Hood Blog 2017) North Korean group definitions are known to have significant overlap, and some security researchers report all North Korean state-sponsored cyber activity under the name [Lazarus Group](https://attack.mitre.org/groups/G0032) instead of tracking clusters or subgroups. | https://attack.mitre.org/groups/G0082 | 29 January 2019 | 17 April 2024 | enterprise-attack,ics-attack | 3.0 |  | BeagleBoyz, Bluenoroff, COPERNICIUM, NICKEL GLADSTONE, Sapphire Sleet, Stardust Chollima | (Citation: CISA AA20-239A BeagleBoyz August 2020), (Citation: Kaspersky Lazarus Under The Hood Blog 2017), (Citation: Microsoft Threat Actor Naming July 2023), (Citation: SecureWorks NICKEL GLADSTONE profile Sept 2021), (Citation: Microsoft Threat Actor Naming July 2023), (Citation: CrowdStrike Stardust Chollima Profile April 2018)(Citation: CrowdStrike GTR 2021 June 2021) | (Citation: ESET Lazarus KillDisk April 2018),,
G1027 | intrusion-set--a07a367a-146c-45a8-a830-d3d337b9befa | CyberAv3ngers | The [CyberAv3ngers](https://attack.mitre.org/groups/G1027) are a suspected Iranian Government Islamic Revolutionary Guard Corps (IRGC)-affiliated APT group. The [CyberAv3ngers](https://attack.mitre.org/groups/G1027) have been known to be active since at least 2020, with disputed and false claims of critical infrastructure compromises in Israel.(Citation: CISA AA23-335A IRGC-Affiliated December 2023) In 2023, the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) engaged in a global targeting and hacking of the Unitronics [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) with [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002). This PLC can be found in multiple sectors, including water and wastewater, energy, food and beverage manufacturing, and healthcare. The most notable feature of this attack was the defacement of the devices user interface.(Citation: CISA AA23-335A IRGC-Affiliated December 2023) | https://attack.mitre.org/groups/G1027 | 25 March 2024 | 10 April 2024 | ics-attack | 1.0 |  | Soldiers of Soloman | CyberAv3ngers reportedly has connections to the IRGC-linked group Soldiers of Solomon.(Citation: CISA AA23-335A IRGC-Affiliated December 2023) | ,,(Citation: CISA AA23-335A IRGC-Affiliated December 2023)
G0035 | intrusion-set--1c63d4ec-0a75-4daa-b1df-0d11af3d3cc1 | Dragonfly | [Dragonfly](https://attack.mitre.org/groups/G0035) is a cyber espionage group that has been attributed to Russia's Federal Security Service (FSB) Center 16.(Citation: DOJ Russia Targeting Critical Infrastructure March 2022)(Citation: UK GOV FSB Factsheet April 2022) Active since at least 2010, [Dragonfly](https://attack.mitre.org/groups/G0035) has targeted defense and aviation companies, government entities, companies related to industrial control systems, and critical infrastructure sectors worldwide through supply chain, spearphishing, and drive-by compromise attacks.(Citation: Symantec Dragonfly)(Citation: Secureworks IRON LIBERTY July 2019)(Citation: Symantec Dragonfly Sept 2017)(Citation: Fortune Dragonfly 2.0 Sept 2017)(Citation: Gigamon Berserk Bear October 2021)(Citation: CISA AA20-296A Berserk Bear December 2020)(Citation: Symantec Dragonfly 2.0 October 2017) | https://attack.mitre.org/groups/G0035 | 31 May 2017 | 08 January 2024 | enterprise-attack,ics-attack | 4.0 | Dragos Threat Intelligence | BROMINE, Berserk Bear, Crouching Yeti, DYMALLOY, Energetic Bear, Ghost Blizzard, IRON LIBERTY, TEMP.Isotope, TG-4192 | (Citation: Microsoft Threat Actor Naming July 2023), (Citation: Gigamon Berserk Bear October 2021)(Citation: DOJ Russia Targeting Critical Infrastructure March 2022)(Citation: UK GOV FSB Factsheet April 2022), (Citation: Secureworks IRON LIBERTY July 2019)(Citation: Gigamon Berserk Bear October 2021)(Citation: DOJ Russia Targeting Critical Infrastructure March 2022)(Citation: UK GOV FSB Factsheet April 2022), (Citation: Dragos DYMALLOY )(Citation: UK GOV FSB Factsheet April 2022), (Citation: Symantec Dragonfly)(Citation: Secureworks IRON LIBERTY July 2019)(Citation: Secureworks MCMD July 2019)(Citation: Secureworks Karagany July 2019)(Citation: Gigamon Berserk Bear October 2021)(Citation: DOJ Russia Targeting Critical Infrastructure March 2022)(Citation: UK GOV FSB Factsheet April 2022), (Citation: Microsoft Threat Actor Naming July 2023), (Citation: Secureworks IRON LIBERTY July 2019)(Citation: Secureworks MCMD July 2019)(Citation: Secureworks Karagany July 2019)(Citation: UK GOV FSB Factsheet April 2022), (Citation: Mandiant Ukraine Cyber Threats January 2022)(Citation: Gigamon Berserk Bear October 2021), (Citation: Secureworks IRON LIBERTY July 2019)(Citation: UK GOV FSB Factsheet April 2022) | (Citation: Symantec Dragonfly),(Citation: Gigamon Berserk Bear October 2021),(Citation: Symantec Security Response July 2014),
G0037 | intrusion-set--2a7914cf-dff3-428d-ab0f-1014d1c28aeb | FIN6 | [FIN6](https://attack.mitre.org/groups/G0037) is a cyber crime group that has stolen payment card data and sold it for profit on underground marketplaces. This group has aggressively targeted and compromised point of sale (PoS) systems in the hospitality and retail sectors.(Citation: FireEye FIN6 April 2016)(Citation: FireEye FIN6 Apr 2019) | https://attack.mitre.org/groups/G0037 | 31 May 2017 | 08 January 2024 | enterprise-attack,ics-attack | 4.0 | Center for Threat-Informed Defense (CTID); Drew Church, Splunk | Camouflage Tempest, ITG08, Magecart Group 6, Skeleton Spider, TAAL | (Citation: Microsoft Threat Actor Naming July 2023), (Citation: Security Intelligence More Eggs Aug 2019), (Citation: Security Intelligence ITG08 April 2020), (Citation: Crowdstrike Global Threat Report Feb 2018), (Citation: Microsoft Threat Actor Naming July 2023) | (Citation: FireEye FIN6 Apr 2019),,
G0046 | intrusion-set--3753cc21-2dae-4dfb-8481-d004e74502cc | FIN7 | [FIN7](https://attack.mitre.org/groups/G0046) is a financially-motivated threat group that has been active since 2013. [FIN7](https://attack.mitre.org/groups/G0046) has primarily targeted the retail, restaurant, hospitality, software, consulting, financial services, medical equipment, cloud services, media, food and beverage, transportation, and utilities industries in the U.S. A portion of [FIN7](https://attack.mitre.org/groups/G0046) was run out of a front company called Combi Security and often used point-of-sale malware for targeting efforts. Since 2020, [FIN7](https://attack.mitre.org/groups/G0046) shifted operations to a big game hunting (BGH) approach including use of [REvil](https://attack.mitre.org/software/S0496) ransomware and their own Ransomware as a Service (RaaS), Darkside. FIN7 may be linked to the [Carbanak](https://attack.mitre.org/groups/G0008) Group, but there appears to be several groups using [Carbanak](https://attack.mitre.org/software/S0030) malware and are therefore tracked separately.(Citation: FireEye FIN7 March 2017)(Citation: FireEye FIN7 April 2017)(Citation: FireEye CARBANAK June 2017)(Citation: FireEye FIN7 Aug 2018)(Citation: CrowdStrike Carbon Spider August 2021)(Citation: Mandiant FIN7 Apr 2022) | https://attack.mitre.org/groups/G0046 | 31 May 2017 | 17 April 2024 | enterprise-attack,ics-attack | 4.0 | Edward Millington | Carbon Spider, ELBRUS, GOLD NIAGARA, ITG14, Sangria Tempest | (Citation: CrowdStrike Carbon Spider August 2021), (Citation: Microsoft Ransomware as a Service), (Citation: Secureworks GOLD NIAGARA Threat Profile), ITG14 shares campaign overlap with [FIN7](https://attack.mitre.org/groups/G0046).(Citation: IBM Ransomware Trends September 2020), (Citation: Microsoft Threat Actor Naming July 2023) | (Citation: IBM Ransomware Trends September 2020),(Citation: Microsoft Ransomware as a Service),(Citation: FBI Flash FIN7 USB),(Citation: CrowdStrike Carbon Spider August 2021),,
G0115 | intrusion-set--c77c5576-ca19-42ed-a36f-4b4486a84133 | GOLD SOUTHFIELD | [GOLD SOUTHFIELD](https://attack.mitre.org/groups/G0115) is a financially motivated threat group active since at least 2018 that operates the [REvil](https://attack.mitre.org/software/S0496) Ransomware-as-a Service (RaaS). [GOLD SOUTHFIELD](https://attack.mitre.org/groups/G0115) provides backend infrastructure for affiliates recruited on underground forums to perpetrate high value deployments. By early 2020, [GOLD SOUTHFIELD](https://attack.mitre.org/groups/G0115) started capitalizing on the new trend of stealing data and further extorting the victim to pay for their data to not get publicly leaked.(Citation: Secureworks REvil September 2019)(Citation: Secureworks GandCrab and REvil September 2019)(Citation: Secureworks GOLD SOUTHFIELD)(Citation: CrowdStrike Evolution of Pinchy Spider July 2021) | https://attack.mitre.org/groups/G0115 | 22 September 2020 | 28 March 2023 | enterprise-attack,ics-attack | 2.0 | Thijn Bukkems, Amazon | Pinchy Spider | (Citation: CrowdStrike Evolution of Pinchy Spider July 2021) | (Citation: Secureworks GandCrab and REvil September 2019),(Citation: Secureworks REvil September 2019),,
G1001 | intrusion-set--f29b7c5e-2439-42ad-a86f-9f8984fafae3 | HEXANE | [HEXANE](https://attack.mitre.org/groups/G1001) is a cyber espionage threat group that has targeted oil & gas, telecommunications, aviation, and internet service provider organizations since at least 2017. Targeted companies have been located in the Middle East and Africa, including Israel, Saudi Arabia, Kuwait, Morocco, and Tunisia. [HEXANE](https://attack.mitre.org/groups/G1001)'s TTPs appear similar to [APT33](https://attack.mitre.org/groups/G0064) and [OilRig](https://attack.mitre.org/groups/G0049) but due to differences in victims and tools it is tracked as a separate entity.(Citation: Dragos Hexane)(Citation: Kaspersky Lyceum October 2021)(Citation: ClearSky Siamesekitten August 2021)(Citation: Accenture Lyceum Targets November 2021) | https://attack.mitre.org/groups/G1001 | 17 October 2018 | 09 February 2024 | enterprise-attack,ics-attack | 2.2 | Dragos Threat Intelligence; Mindaugas Gudzis, BT Security | Lyceum, Siamesekitten, Spirlin | (Citation: SecureWorks August 2019), (Citation: ClearSky Siamesekitten August 2021), (Citation: Accenture Lyceum Targets November 2021) | ,,
G0032 | intrusion-set--c93fccb1-e8e8-42cf-ae33-2ad1d183913a | Lazarus Group | [Lazarus Group](https://attack.mitre.org/groups/G0032) is a North Korean state-sponsored cyber threat group that has been attributed to the Reconnaissance General Bureau.(Citation: US-CERT HIDDEN COBRA June 2017)(Citation: Treasury North Korean Cyber Groups September 2019) The group has been active since at least 2009 and was reportedly responsible for the November 2014 destructive wiper attack against Sony Pictures Entertainment as part of a campaign named Operation Blockbuster by Novetta. Malware used by [Lazarus Group](https://attack.mitre.org/groups/G0032) correlates to other reported campaigns, including Operation Flame, Operation 1Mission, Operation Troy, DarkSeoul, and Ten Days of Rain.(Citation: Novetta Blockbuster) North Korean group definitions are known to have significant overlap, and some security researchers report all North Korean state-sponsored cyber activity under the name [Lazarus Group](https://attack.mitre.org/groups/G0032) instead of tracking clusters or subgroups, such as [Andariel](https://attack.mitre.org/groups/G0138), [APT37](https://attack.mitre.org/groups/G0067), [APT38](https://attack.mitre.org/groups/G0082), and [Kimsuky](https://attack.mitre.org/groups/G0094). | https://attack.mitre.org/groups/G0032 | 31 May 2017 | 11 April 2024 | enterprise-attack,ics-attack | 4.0 | Dragos Threat Intelligence; Kyaw Pyiyt Htet, @KyawPyiytHtet | Diamond Sleet, Guardians of Peace, HIDDEN COBRA, Labyrinth Chollima, NICKEL ACADEMY, ZINC | (Citation: Microsoft Threat Actor Naming July 2023), (Citation: US-CERT HIDDEN COBRA June 2017), The U.S. Government refers to malicious cyber activity by the North Korean government as HIDDEN COBRA.(Citation: US-CERT HIDDEN COBRA June 2017)(Citation: US-CERT HOPLIGHT Apr 2019), (Citation: CrowdStrike Labyrinth Chollima Feb 2022), (Citation: Secureworks NICKEL ACADEMY Dec 2017), (Citation: Microsoft ZINC disruption Dec 2017) | (Citation: FireEye WannaCry 2017),(Citation: FireEye APT38 Oct 2018),(Citation: LogRhythm WannaCry),(Citation: SecureWorks WannaCry Analysis),(Citation: Eduard Kovacs March 2018),(Citation: Novetta Threat Research Group February 2016),
G0049 | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | OilRig | [OilRig](https://attack.mitre.org/groups/G0049) is a suspected Iranian threat group that has targeted Middle Eastern and international victims since at least 2014. The group has targeted a variety of sectors, including financial, government, energy, chemical, and telecommunications. It appears the group carries out supply chain attacks, leveraging the trust relationship between organizations to attack their primary targets. The group works on behalf of the Iranian government based on infrastructure details that contain references to Iran, use of Iranian infrastructure, and targeting that aligns with nation-state interests.(Citation: FireEye APT34 Dec 2017)(Citation: Palo Alto OilRig April 2017)(Citation: ClearSky OilRig Jan 2017)(Citation: Palo Alto OilRig May 2016)(Citation: Palo Alto OilRig Oct 2016)(Citation: Unit42 OilRig Playbook 2023)(Citation: Unit 42 QUADAGENT July 2018) | https://attack.mitre.org/groups/G0049 | 14 December 2017 | 11 April 2024 | enterprise-attack,ics-attack | 4.0 | Bryan Lee; Dragos Threat Intelligence; Robert Falcone | APT34, COBALT GYPSY, EUROPIUM, Evasive Serpens, Hazel Sandstorm, Helix Kitten, IRN2 | This group was previously tracked under two distinct groups, APT34 and OilRig, but was combined due to additional reporting giving higher confidence about the overlap of the activity.(Citation: Unit 42 QUADAGENT July 2018)(Citation: FireEye APT34 Dec 2017)(Citation: Check Point APT34 April 2021), (Citation: Secureworks COBALT GYPSY Threat Profile), (Citation: Microsoft Threat Actor Naming July 2023), (Citation: Unit42 OilRig Playbook 2023), (Citation: Microsoft Threat Actor Naming July 2023), (Citation: Unit 42 QUADAGENT July 2018)(Citation: Crowdstrike Helix Kitten Nov 2018), (Citation: Crowdstrike Helix Kitten Nov 2018) | ,(Citation: Robert Falcone, Bryan Lee May 2016),(Citation: Eduard Kovacs May 2018),(Citation: Dragos),
G0034 | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | Sandworm Team | [Sandworm Team](https://attack.mitre.org/groups/G0034) is a destructive threat group that has been attributed to Russia's General Staff Main Intelligence Directorate (GRU) Main Center for Special Technologies (GTsST) military unit 74455.(Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: UK NCSC Olympic Attacks October 2020) This group has been active since at least 2009.(Citation: iSIGHT Sandworm 2014)(Citation: CrowdStrike VOODOO BEAR)(Citation: USDOJ Sandworm Feb 2020)(Citation: NCSC Sandworm Feb 2020) In October 2020, the US indicted six GRU Unit 74455 officers associated with [Sandworm Team](https://attack.mitre.org/groups/G0034) for the following cyber operations: the 2015 and 2016 attacks against Ukrainian electrical companies and government organizations, the 2017 worldwide [NotPetya](https://attack.mitre.org/software/S0368) attack, targeting of the 2017 French presidential campaign, the 2018 [Olympic Destroyer](https://attack.mitre.org/software/S0365) attack against the Winter Olympic Games, the 2018 operation against the Organisation for the Prohibition of Chemical Weapons, and attacks against the country of Georgia in 2018 and 2019.(Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: UK NCSC Olympic Attacks October 2020) Some of these were conducted with the assistance of GRU Unit 26165, which is also referred to as [APT28](https://attack.mitre.org/groups/G0007).(Citation: US District Court Indictment GRU Oct 2018) | https://attack.mitre.org/groups/G0034 | 31 May 2017 | 06 April 2024 | enterprise-attack,ics-attack,mobile-attack | 4.0 | Dragos Threat Intelligence | BlackEnergy (Group), ELECTRUM, FROZENBARENTS, IRIDIUM, IRON VIKING, Quedagh, Seashell Blizzard, Telebots, Voodoo Bear | (Citation: NCSC Sandworm Feb 2020)(Citation: UK NCSC Olympic Attacks October 2020), (Citation: Dragos ELECTRUM)(Citation: UK NCSC Olympic Attacks October 2020), (Citation: Leonard TAG 2023), (Citation: Microsoft Prestige ransomware October 2022), (Citation: Secureworks IRON VIKING )(Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: UK NCSC Olympic Attacks October 2020), (Citation: iSIGHT Sandworm 2014) (Citation: F-Secure BlackEnergy 2014)(Citation: UK NCSC Olympic Attacks October 2020), (Citation: Microsoft Threat Actor Naming July 2023), (Citation: NCSC Sandworm Feb 2020)(Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: UK NCSC Olympic Attacks October 2020), (Citation: CrowdStrike VOODOO BEAR)(Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: UK NCSC Olympic Attacks October 2020) | (Citation: NCSC Sandworm Feb 2020),(Citation: UK NCSC Olympic Attacks October 2020),(Citation: Secureworks IRON VIKING),(Citation: ESET Industroyer),(Citation: iSIGHT Sandworm 2014),(Citation: Dragos Crashoverride 2018),(Citation: Trend Micro Cyclops Blink March 2022),(Citation: US District Court Indictment GRU Unit 74455 October 2020),(Citation: Dragos Crashoverride 2017),(Citation: Industroyer2 ESET April 2022),(Citation: F-Secure BlackEnergy 2014),(Citation: Secureworks IRON VIKING ),(Citation: ICS CERT September 2018),(Citation: Dragos October 2018),(Citation: Dragos Inc. June 2017),(Citation: ICS-CERT December 2014),(Citation: Joe Slowik August 2019),(Citation: Dragos-Sandworm-Ukraine-2022),(Citation: Andy Greenberg June 2017),(Citation: Mandiant-Sandworm-Ukraine-2022),(Citation: US District Court Indictment GRU Unit 74455 October 2020)
G0088 | intrusion-set--9538b1a4-4120-4e2d-bf59-3b11fcab05a4 | TEMP.Veles | [TEMP.Veles](https://attack.mitre.org/groups/G0088) is a Russia-based threat group that has targeted critical infrastructure. The group has been observed utilizing [TRITON](https://attack.mitre.org/software/S0609), a malware framework designed to manipulate industrial safety systems.(Citation: FireEye TRITON 2019)(Citation: FireEye TEMP.Veles 2018)(Citation: FireEye TEMP.Veles JSON April 2019) | https://attack.mitre.org/groups/G0088 | 16 April 2019 | 17 April 2024 | enterprise-attack,ics-attack | 1.4 | Dragos Threat Intelligence | XENOTIME | The activity group XENOTIME, as defined by Dragos, has overlaps with activity reported upon by FireEye about TEMP.Veles as well as the actors behind [TRITON](https://attack.mitre.org/software/S0609).(Citation: Dragos Xenotime 2018)(Citation: Pylos Xenotime 2019)(Citation: FireEye TRITON 2019)(Citation: FireEye TEMP.Veles 2018) | (Citation: Dragos Xenotime 2018),(Citation: Chris Bing May 2018),(Citation: Dragos Threat Intelligence August 2019),(Citation: FireEye TRITON Dec 2017),(Citation: FireEye TEMP.Veles 2018)
G0102 | intrusion-set--dd2d9ca6-505b-4860-a604-233685b802c7 | Wizard Spider | [Wizard Spider](https://attack.mitre.org/groups/G0102) is a Russia-based financially motivated threat group originally known for the creation and deployment of [TrickBot](https://attack.mitre.org/software/S0266) since at least 2016. [Wizard Spider](https://attack.mitre.org/groups/G0102) possesses a diverse aresenal of tools and has conducted ransomware campaigns against a variety of organizations, ranging from major corporations to hospitals.(Citation: CrowdStrike Ryuk January 2019)(Citation: DHS/CISA Ransomware Targeting Healthcare October 2020)(Citation: CrowdStrike Wizard Spider October 2020) | https://attack.mitre.org/groups/G0102 | 12 May 2020 | 03 April 2024 | enterprise-attack,ics-attack | 4.0 | Edward Millington; Oleksiy Gayda | DEV-0193, FIN12, GOLD BLACKBURN, Grim Spider, ITG23, Periwinkle Tempest, TEMP.MixMaster, UNC1878 | (Citation: Microsoft Threat Actor Naming July 2023), (Citation: Mandiant FIN12 Oct 2021), (Citation: Secureworks Gold Blackburn Mar 2022), (Citation: CrowdStrike Ryuk January 2019)(Citation: CrowdStrike Grim Spider May 2019), (Citation: IBM X-Force ITG23 Oct 2021), (Citation: Microsoft Threat Actor Naming July 2023), (Citation: FireEye Ryuk and Trickbot January 2019), (Citation: FireEye KEGTAP SINGLEMALT October 2020) | (Citation: Mandiant FIN12 Oct 2021),(Citation: DFIR Ryuk 2 Hour Speed Run November 2020),(Citation: DFIR Ryuk in 5 Hours October 2020),(Citation: FireEye KEGTAP SINGLEMALT October 2020),(Citation: CrowdStrike Wizard Spider October 2020),(Citation: Microsoft Ransomware as a Service),(Citation: DFIR Ryuk's Return October 2020),(Citation: CrowdStrike Ryuk January 2019),(Citation: Sophos New Ryuk Attack October 2020),(Citation: Red Canary Hospital Thwarted Ryuk October 2020),(Citation: DHS/CISA Ransomware Targeting Healthcare October 2020),,

## campaigns
ID | STIX ID | name | description | url | created | last modified | domain | version | associated campaigns | associated campaigns citations | first seen | first seen citation | last seen | last seen citation | relationship citations
C0028 | campaign--46421788-b6e1-4256-b351-f8beffd1afba | 2015 Ukraine Electric Power Attack | [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028) was a [Sandworm Team](https://attack.mitre.org/groups/G0034) campaign during which they used [BlackEnergy](https://attack.mitre.org/software/S0089) (specifically BlackEnergy3) and [KillDisk](https://attack.mitre.org/software/S0607) to target and disrupt transmission and distribution substations within the Ukrainian power grid. This campaign was the first major public attack conducted against the Ukrainian power grid by Sandworm Team. | https://attack.mitre.org/campaigns/C0028 | 27 September 2023 | 06 October 2023 | ics-attack,enterprise-attack | 1.0 |  |  | 01 December 2015 | (Citation: Booz Allen Hamilton) | 01 January 2016 | (Citation: Booz Allen Hamilton) | (Citation: Booz Allen Hamilton),(Citation: Andy Greenberg June 2017),(Citation: Charles McLellan March 2016),(Citation: Ukraine15 - EISAC - 201603),(Citation: Booz Allen Hamilton),(Citation: Andy Greenberg June 2017),(Citation: US District Court Indictment GRU Unit 74455 October 2020)
C0025 | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | 2016 Ukraine Electric Power Attack | [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025) was a [Sandworm Team](https://attack.mitre.org/groups/G0034) campaign during which they used [Industroyer](https://attack.mitre.org/software/S0604) malware to target and disrupt distribution substations within the Ukrainian power grid. This campaign was the second major public attack conducted against Ukraine by [Sandworm Team](https://attack.mitre.org/groups/G0034).(Citation: ESET Industroyer)(Citation: Dragos Crashoverride 2018) | https://attack.mitre.org/campaigns/C0025 | 31 March 2023 | 10 April 2023 | enterprise-attack,ics-attack | 1.0 |  |  | 01 December 2016 | (Citation: ESET Industroyer)(Citation: Dragos Crashoverride 2018) | 01 December 2016 | (Citation: ESET Industroyer)(Citation: Dragos Crashoverride 2018) | (Citation: Dragos Crashoverride 2018),(Citation: ESET Industroyer),(Citation: Dragos Crashoverride 2018),(Citation: ESET Industroyer),(Citation: Joe Slowik August 2019),(Citation: US District Court Indictment GRU Unit 74455 October 2020)
C0034 | campaign--df8eb785-70f8-4300-b444-277ba849083d | 2022 Ukraine Electric Power Attack | The [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034) was a [Sandworm Team](https://attack.mitre.org/groups/G0034) campaign that used a combination of GOGETTER, Neo-REGEORG, [CaddyWiper](https://attack.mitre.org/software/S0693), and living of the land (LotL) techniques to gain access to a Ukrainian electric utility to send unauthorized commands from their SCADA system.(Citation: Mandiant-Sandworm-Ukraine-2022)(Citation: Dragos-Sandworm-Ukraine-2022) | https://attack.mitre.org/campaigns/C0034 | 27 March 2024 | 10 April 2024 | enterprise-attack,ics-attack | 1.0 |  |  | 01 June 2022 | (Citation: Mandiant-Sandworm-Ukraine-2022) | 01 October 2022 | (Citation: Mandiant-Sandworm-Ukraine-2022) | ,(Citation: Mandiant-Sandworm-Ukraine-2022),(Citation: Dragos-Sandworm-Ukraine-2022),(Citation: Mandiant-Sandworm-Ukraine-2022)
C0020 | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | Maroochy Water Breach | [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020) was an incident in 2000 where an adversary leveraged the local government’s wastewater control system and stolen engineering equipment to disrupt and eventually release 800,000 liters of raw sewage into the local community.(Citation: Marshall Abrams July 2008) | https://attack.mitre.org/campaigns/C0020 | 10 March 2023 | 05 April 2023 | ics-attack | 1.0 |  |  | 01 February 2000 | (Citation: Marshall Abrams July 2008) | 01 April 2000 | (Citation: Marshall Abrams July 2008) | ,(Citation: Marshall Abrams July 2008),
C0030 | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | Triton Safety Instrumented System Attack | [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030) was a campaign employed by [TEMP.Veles](https://attack.mitre.org/groups/G0088) which leveraged the [Triton](https://attack.mitre.org/software/S1009) malware framework against a petrochemical organization.(Citation: Triton-EENews-2017) The malware and techniques used within this campaign targeted specific Triconex [Safety Controller](https://attack.mitre.org/assets/A0010)s within the environment.(Citation: FireEye TRITON 2018) The incident was eventually discovered due to a safety trip that occurred as a result of an issue in the malware.(Citation: FireEye TRITON 2017) | https://attack.mitre.org/campaigns/C0030 | 25 March 2024 | 17 April 2024 | ics-attack,enterprise-attack | 1.0 |  |  | 01 June 2017 | (Citation: Triton-EENews-2017) | 01 August 2017 | (Citation: Triton-EENews-2017) | (Citation: FireEye TRITON 2018),(Citation: FireEye TRITON Dec 2017),(Citation: FireEye TEMP.Veles 2018),(Citation: FireEye TRITON 2018),(Citation: Triton-EENews-2017),(Citation: FireEye TRITON Dec 2017),(Citation: FireEye TEMP.Veles 2018),(Citation: FireEye TRITON Dec 2017),(Citation: FireEye TEMP.Veles 2018)
C0031 | campaign--8fda050f-470d-4401-994e-35c1a6c301de | Unitronics Defacement Campaign | The [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031) was a collection of intrusions across multiple sectors by the [CyberAv3ngers](https://attack.mitre.org/groups/G1027), where threat actors engaged in a seemingly opportunistic and global targeting and defacement of Unitronics Vision Series [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) with [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002). The sectors that these PLCs can be commonly found in are water and wastewater, energy, food and beverage manufacturing, and healthcare. The most notable feature of this attack was the defacement of the PLCs' HMIs.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: Frank Bajak and Marc Levy December 2023) | https://attack.mitre.org/campaigns/C0031 | 25 March 2024 | 15 April 2024 | ics-attack | 1.0 |  |  | 01 November 2023 | (Citation: CISA AA23-335A IRGC-Affiliated December 2023) | 01 November 2023 | (Citation: Lisa Zahner December 2023) | ,(Citation: WPXI Aliquippa Water November 2023),(Citation: Jamie Tarabay and Katrina Manson December 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023),(Citation: Frank Bajak and Marc Levy December 2023),(Citation: CISA Unitronics November 2023),(Citation: Lisa Zahner December 2023),(Citation: CISA AA23-335A IRGC-Affiliated December 2023)

## assets
ID | STIX ID | name | description | url | created | last modified | domain | version | platforms | sectors | related assets | related assets sectors | related assets description | relationship citations
A0008 | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | Application Server | Application servers are used across many different sectors to host various diverse software applications necessary to supporting the ICS. Example functions can include data analytics and reporting, alarm management, and the management/coordination of different control servers. The application server typically runs on a modern server operating system (e.g., MS Windows Server). | https://attack.mitre.org/assets/A0008 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Linux, Windows | General
A0007 | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | Control Server | Control servers are typically a software platform that runs on a modern server operating system (e.g., MS Windows Server). The server typically uses one or more automation protocols (e.g., Modbus, DNP3) to communicate with the various low-level control devices such as Remote Terminal Units (RTUs) and Programmable Logic Controllers (PLCs). The control server also usually provides an interface/network service to connect with an HMI. | https://attack.mitre.org/assets/A0007 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Linux, Windows | General | Supervisory Control And Data Acquisition (SCADA) Server; Master Terminal Unit (MTU); Supervisory controller; Distribution/Energy Management System (DMS/EMS) | Electric, General, Water and Wastewater; General; General; Electric | A SCADA server is used to perform monitoring and control across a distributed environment. It typically has an associated HMI to provide information to a human operator and heavily depends on the human operator to initiate control actions.; *A controller that also acts as a server that hosts the control software that communicates with lower-level control devices, such as remote terminal units (RTUs) and programmable logic controllers (PLCs), over an ICS network* (Citation: Guidance - NIST SP800-82); *A controller that also acts as a server that hosts the control software that communicates with lower-level control devices, such as remote terminal units (RTUs) and programmable logic controllers (PLCs), over an ICS network* (Citation: Guidance - NIST SP800-82); A DMS and EMS are electric sector specific devices that are commonly used to manage distribution and transmission-level electrical grids. These platforms typically integrate a SCADA server and HMI with domain-specific data analysis applications, such as state-estimation and contingency analysis (EMS), or voltage-var control or fault restoration (DMS).
A0009 | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | Data Gateway | Data Gateway is a device that supports the communication and exchange of data between different systems, networks, or protocols within the ICS. Different types of data gateways are used to perform various functions, including: * <u>Protocol Translation:</u> Enable communication to devices that support different or incompatible protocols by translating information from one protocol to another. * <u>Media Converter:</u> Convert data across different Layer 1 and 2 network protocols / mediums, for example, converting from Serial to Ethernet. * <u>Data Aggregation:</u> Collect and combine data from different devices into one consistent format and protocol interface. Data gateways are often critical to the forwarding/transmission of critical control or monitoring data within the ICS. Further, these devices often have remote various network services that are used to communicate across different zones or networks. These assets may focus on a single function listed below or combinations of these functions to best fit the industry use-case. | https://attack.mitre.org/assets/A0009 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Embedded, Linux, Windows | General | Data Acquisition Server (DAS); Serial to Ethernet Gateway | General; Electric, General | A Data Acquisition Server (DAS) a system or software platform that is used to collect, aggregate, and store data/telemetry from field devices using various SCADA/Automation protocols. ; A Serial to Ethernet gateway is a device that is used to connect field devices that only support serial-based communication (e.g., RS-232) with more modern Ethernet-based networks.
A0006 | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | Data Historian | Data historians, or historian, are systems used to collect and store data, including telemetry, events, alerts, and alarms about the operational process and supporting devices. The historian typically utilizes a database to store this data, and commonly provide tools and interfaces to support the analysis of the data. Data historians are often used to support various engineering or business analysis functions and therefore commonly needs access from the corporate network. Data historians often work in a hierarchical paradigm where lower/site level historians collect and store data which is then aggregated into a site/plant level historian. Therefore, data historians often have remote services that can be accessed externally from the ICS network. | https://attack.mitre.org/assets/A0006 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Embedded, Linux, Windows | General
A0013 | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | Field I/O | Field I/O are devices that communicate with a controller or data aggregator to either send input data or receive output data. Input data may include readings about a given environment/device state from sensors, while output data may include data sent back to actuators for them to either undertake actions or change parameter values.(Citation: Guidance - NIST SP800-82) These devices are frequently embedded devices running on lightweight embedded operating systems or RTOSes. | https://attack.mitre.org/assets/A0013 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Embedded |  | Smart Sensors; Variable Frequency Drive (VFD) | General; General | *A device that procures a voltage or current output that is representative of some physical property being measured (e.g., speed, temperature, flow).* (Citation: Guidance - NIST SP800-82) Smart sensors take this functionality and add on on-device processing and network communication.; *A type of drive that controls the speed, but not the precise position, of a non-servo, AC motor by varying the frequency of the electricity going to that motor. VFDs are typically used for applications where speed and power are important, but precise positioning is not.* (Citation: Guidance - NIST SP800-82) VFDs can be network connected.
A0002 | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | Human-Machine Interface (HMI) | Human-Machine Interfaces (HMIs) are systems used by an operator to monitor the real-time status of an operational process and to perform necessary control functions, including the adjustment of device parameters. An HMI can take various forms, including a dedicated screen or control panel integrated with a specific device/controller, or a customizable software GUI application running on a standard operating system (e.g., MS Windows) that interfaces with a control/SCADA server. The HMI is critical to ensuring operators have sufficient visibility and control over the operational process. | https://attack.mitre.org/assets/A0002 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Linux, Windows | General | Operator Workstation (OWS) | General | An Operator Workstation (OWS) or Console is a system or device used by an operator to interface with a control system, including to access/visualizes key information or parameters about the operational process and initiate control actions. This typically consists of specialized OWS software installed on a Workstation platform. (Citation: IEC February 2019)
A0005 | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | Intelligent Electronic Device (IED) | An Intelligent Electronic Device (IED) is a type of specialized field device that is designed to perform specific operational functions, frequently for protection, monitoring, or control within the electric sector. IEDs are typically used to both acquire telemetry and execute tailored control algorithms/actions based on customizable parameters/settings. An IED is usually implemented as a dedicated embedded device and supports various network automation protocols to communicate with RTUs and Control Servers. | https://attack.mitre.org/assets/A0005 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Embedded | Electric | Protection Relay; Field Device / Controller | Electric; | A protection relay is a type of IED used within the electric sector to monitor for faults or problematic operating conditions on power lines, busses, or transformers. While traditionally protection relays were electromechanical or electromagnetic devices, modern relays utilize microprocessors, embedded operating system, and SCADA communications.; IEDs may be referred to as Field Controllers or Field Devices as a general function name.
A0012 | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | Jump Host | Jump hosts are devices used to support remote management sessions into ICS networks or devices. The system is used to access the ICS environment securely from external networks, such as the corporate network. The user must first remote into the jump host before they can access ICS devices. The jump host may be a customized Windows server using common remote access protocols (e.g., RDP) or a dedicated access management device. The jump host typically performs various security functions to ensure the authenticity of remote sessions, including authentication, enforcing access controls/permissions, and auditing all access attempts. | https://attack.mitre.org/assets/A0012 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Embedded, Linux, Windows | General | Intermediate System | Electric | A Cyber Asset or collection of Cyber Assets performing access control to restrict Interactive Remote Access to only authorized users.(Citation: North American Electric Reliability Corporation June 2021)
A0003 | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | Programmable Logic Controller (PLC) | A Programmable Logic Controller (PLC) is an embedded programmable control device. PLCs typically utilize a modular architecture with separate modules used to support its processing capabilities, communication mediums, and I/O interfaces. PLCs allow for the deployment of customized programs/logic to control or monitor an operational process. This logic is defined using industry specific programming languages, such as IEC 61131 (Citation: IEC February 2013), which define the set of tasks and program organizational units (POUs) included in the device’s programs. PLCs also typically have distinct operating modes (e.g., Remote, Run, Program, Stop) which are used to determine when the device can be programmed or whether it should execute the custom logic. | https://attack.mitre.org/assets/A0003 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Embedded | General | Process Automation Controller (PAC); Field Device / Controller | General; | Process Automation Controllers (PAC) share much of the same functionality as a PLC. PACs may include advanced features for process control, motion control, drive control, and vision applications. PACs may include additional features such as options to program in traditional programming languages such as C and C++ in addition to 61131 programming languages in order to support these more advanced controls. ; Programmable Logic Controller (PLC) may be referred to as Field Controllers or Field Devices as a general function name.
A0004 | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | Remote Terminal Unit (RTU) | A Remote Terminal Unit (RTU) is a device that typically resides between field devices (e.g., PLCs, IEDs) and control/SCADA servers and supports various communication interfacing and data aggregation functions. RTUs are typically responsible for forwarding commands from the control server and the collection of telemetry, events, and alerts from the field devices. An RTU can be implemented as a dedicated embedded device, as software platform that runs on a hardened/ruggedized computer, or using a custom application program on a PLC. | https://attack.mitre.org/assets/A0004 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Embedded, Linux, Windows | Electric, General, Water and Wastewater
A0014 | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | Routers | A computer that is a gateway between two networks at OSI layer 3 and that relays and directs data packets through that inter-network. The most common form of router operates on IP packets.(Citation: IETF RFC4949 2007) | https://attack.mitre.org/assets/A0014 | 29 September 2023 | 16 October 2023 | ICS | 1.0 | Embedded | General
A0010 | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | Safety Controller | Safety controllers are typically a type of field device used to perform the safety critical function. Safety controllers often support the deployment of custom programs/logic, similar to a PLC, but can also be tailored for sector specific functions/applications. The safety controllers typically utilize redundant hardware and processors to ensure they operate reliably if a component fails. | https://attack.mitre.org/assets/A0010 | 28 September 2023 | 16 October 2023 | ICS | 1.0 | Embedded |  | Safety Instrumented System (SIS) controller; Emergency Shutdown Systems (ESD) controller; Burner Management Systems (BMS) controller | ; ; | SIS controllers are used to “take the process to a safe state when predetermined conditions are violated” (Citation: Guidance - NIST SP800-82) through the reading of sensor data and interaction with digital/physical control surfaces. These devices are oftentimes located on programmable embedded devices running specialized RTOS or other embedded operating systems. ; Emergency Shutdown System controllers are used to read sensor values and interact with control surfaces to return the system “to a safe static condition so that any remedial action can be taken”. (Citation: SIGTTO ESD 2021); Burner Management System controllers are used to interact with sensors and control surfaces to maintain safe operating conditions for the burner. These can include safely starting-up and managing the main flame, controlling and monitoring the burning conditions, and safely initiating planned or unplanned shutdown sequences.
A0011 | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | Virtual Private Network (VPN) Server | A VPN server is a device that is used to establish a secure network tunnel between itself and other remote VPN devices, including field VPNs. VPN servers can be used to establish a secure connection with a single remote device, or to securely bridge all traffic between two separate networks together by encapsulating all data between those networks. VPN servers typically support remote network services that are used by field VPNs to initiate the establishment of the secure VPN tunnel between the field device and server. | https://attack.mitre.org/assets/A0011 | 28 September 2023 | 04 October 2023 | ICS | 1.0 | Embedded, Linux, Windows | General | Virtual Private Network (VPN) terminator; Field VPN | General; General | A VPN terminator is a device performs the role of either a VPN client or server to support the establishment of VPN connection. (Citation: IEC February 2019); Field VPN are typically deployed at remote outstations and are used to create secure connections to VPN servers within data/control center environments.
A0001 | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | Workstation | Workstations are devices used by human operators or engineers to perform various configuration, programming, maintenance, diagnostic, or operational tasks. Workstations typically utilize standard desktop or laptop hardware and operating systems (e.g., MS Windows), but run dedicated control system applications or diagnostic/management software to support interfacing with the control servers or field devices. Some workstations have a fixed location within the network architecture, while others are transient devices that are directly connected to various field devices to support local management activities. | https://attack.mitre.org/assets/A0001 | 28 September 2023 | 28 September 2023 | ICS | 1.0 | Windows | General | Transient Cyber Asset (TCA); Engineering Workstation (EWS) | Electric; General | A Transient Cyber Asset (TCA)(Citation: North American Electric Reliability Corporation June 2021) is a mobile workstation that is used to support management functions across multiple different networks, rather than being dedicated to any specific device/network. The TCA is often used to directly manage ICS environments that do not have any dedicated support for external remote access. Therefore, the TCA provides a mechanism for connectivity and file transfer to many networks/devices, even if they are segmented or “air gapped” from other networks. ; An Engineering Workstation (EWS) is used to perform various maintenance, configuration, or diagnostics functions for a control system. The EWS will likely require dedicated application software to interface with various devices (e.g., RTUs, PLCs), and may be used to transfer data or files between the control system devices and other networks.

## mitigations
ID | STIX ID | name | description | url | created | last modified | domain | version | relationship citations
M0801 | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | Access Management | Access Management technologies can be used to enforce authorization polices and decisions, especially when existing field devices do not provided sufficient capabilities to support user identification and authentication. (Citation: McCarthy, J et al. July 2018) These technologies typically utilize an in-line network device or gateway system to prevent access to unauthenticated users, while also integrating with an authentication service to first verify user credentials. (Citation: Centre for the Protection of National Infrastructure November 2010) | https://attack.mitre.org/mitigations/M0801 | 11 September 2020 | 19 September 2023 | ics-attack | 1.0 | (Citation: McCarthy, J et al. July 2018)
M0936 | course-of-action--86b455f2-fb63-4043-93a8-32a3a7703a02 | Account Use Policies | Configure features related to account use like login attempt lockouts, specific login times, etc. | https://attack.mitre.org/mitigations/M0936 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Keith Stouffer May 2015)
M0915 | course-of-action--2f0160b7-e982-49d7-9612-f19b810f1722 | Active Directory Configuration | Configure Active Directory to prevent use of certain techniques; use security identifier (SID) Filtering, etc. | https://attack.mitre.org/mitigations/M0915 | 06 June 2019 | 24 October 2022 | ics-attack | 1.0 | (Citation: Schweitzer Engineering Laboratories August 2015),(Citation: Keith Stouffer May 2015)
M0949 | course-of-action--faf2b40e-5981-433f-aa46-17458e0026f7 | Antivirus/Antimalware | Use signatures or heuristics to detect malicious software. Within industrial control environments, antivirus/antimalware installations should be limited to assets that are not involved in critical or real-time operations. To minimize the impact to system availability, all products should first be validated within a representative test environment before deployment to production systems. (Citation: NCCIC August 2018) | https://attack.mitre.org/mitigations/M0949 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0
M0913 | course-of-action--8a3aadd0-b5f4-433a-800e-4893e4196bb7 | Application Developer Guidance | This mitigation describes any guidance or training given to developers of applications to avoid introducing security weaknesses that an adversary may be able to take advantage of. | https://attack.mitre.org/mitigations/M0913 | 25 October 2017 | 19 September 2023 | ics-attack | 1.0 | (Citation: CISA June 2013)
M0948 | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | Application Isolation and Sandboxing | Restrict the execution of code to a virtual environment on or in-transit to an endpoint system. | https://attack.mitre.org/mitigations/M0948 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Dan Goodin March 2017)
M0947 | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | Audit | Perform audits or scans of systems, permissions, insecure software, insecure configurations, etc. to identify potential weaknesses. Perform periodic integrity checks of the device to validate the correctness of the firmware, software, programs, and configurations. Integrity checks, which typically include cryptographic hashes or digital signatures, should be compared to those obtained at known valid states, especially after events like device reboots, program downloads, or program restarts. | https://attack.mitre.org/mitigations/M0947 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: IEC February 2019),(Citation: National Security Agency February 2016),(Citation: Emerson Exchange)
M0800 | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | Authorization Enforcement | The device or system should restrict read, manipulate, or execute privileges to only authenticated users who require access based on approved security policies. Role-based Access Control (RBAC) schemes can help reduce the overhead of assigning permissions to the large number of devices within an ICS. For example, IEC 62351 provides examples of roles used to support common system operations within the electric power sector (Citation: International Electrotechnical Commission July 2020), while IEEE 1686 defines standard permissions for users of IEDs. (Citation: Institute of Electrical and Electronics Engineers January 2014) | https://attack.mitre.org/mitigations/M0800 | 11 September 2020 | 20 October 2023 | ics-attack | 1.1 | (Citation: MITRE June 2020)
M0946 | course-of-action--8ac1d6e1-b07f-476a-9732-84984ebc2405 | Boot Integrity | Use secure methods to boot a system and verify the integrity of the operating system and loading mechanisms. | https://attack.mitre.org/mitigations/M0946 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Intel),(Citation: N/A),(Citation: ESET Research Whitepapers September 2018)
M0945 | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | Code Signing | Enforce binary and application integrity with digital signature verification to prevent untrusted code from executing. | https://attack.mitre.org/mitigations/M0945 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0
M0802 | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | Communication Authenticity | When communicating over an untrusted network, utilize secure network protocols that both authenticate the message sender and can verify its integrity. This can be done either through message authentication codes (MACs) or digital signatures, to detect spoofed network messages and unauthorized connections. | https://attack.mitre.org/mitigations/M0802 | 11 September 2020 | 19 September 2023 | ics-attack | 1.0 | (Citation: CISA March 2010)
M0953 | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | Data Backup | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of 'gold-copy' back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | https://attack.mitre.org/mitigations/M0953 | 19 July 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Department of Homeland Security October 2009),(Citation: National Institute of Standards and Technology April 2013)
M0803 | course-of-action--337c4e2a-21a7-4d9a-bfee-9efd6cebf0e5 | Data Loss Prevention | Data Loss Prevention (DLP) technologies can be used to help identify adversarial attempts to exfiltrate operational information, such as engineering plans, trade secrets, recipes, intellectual property, or process telemetry. DLP functionality may be built into other security products such as firewalls or standalone suites running on the network and host-based agents. DLP may be configured to prevent the transfer of information through corporate resources such as email, web, and physical media such as USB for host-based solutions. | https://attack.mitre.org/mitigations/M0803 | 11 September 2020 | 30 March 2023 | ics-attack | 1.0
M0942 | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | Disable or Remove Feature or Program | Remove or deny access to unnecessary and potentially vulnerable software to prevent abuse by adversaries. | https://attack.mitre.org/mitigations/M0942 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Department of Homeland Security September 2016)
M0808 | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | Encrypt Network Traffic | Utilize strong cryptographic techniques and protocols to prevent eavesdropping on network communications. | https://attack.mitre.org/mitigations/M0808 | 11 September 2020 | 19 September 2023 | ics-attack | 1.0 | (Citation: Bastille April 2017),(Citation: Keith Stouffer May 2015)
M0941 | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | Encrypt Sensitive Information | Protect sensitive data-at-rest with strong encryption. | https://attack.mitre.org/mitigations/M0941 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Keith Stouffer May 2015),(Citation: National Institute of Standards and Technology April 2013)
M0938 | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | Execution Prevention | Block execution of code on a system through application control, and/or script blocking. | https://attack.mitre.org/mitigations/M0938 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0
M0950 | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | Exploit Protection | Use capabilities to detect and block conditions that may lead to or be indicative of a software exploit occurring. | https://attack.mitre.org/mitigations/M0950 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: Microsoft Security Response Center August 2017),(Citation: Wikipedia)
M0937 | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | Filter Network Traffic | Use network appliances to filter ingress or egress traffic and perform protocol-based filtering. Configure software on endpoints to filter network traffic. Perform inline allow/denylisting of network messages based on the application layer (OSI Layer 7) protocol, especially for automation protocols. Application allowlists are beneficial when there are well-defined communication sequences, types, rates, or patterns needed during expected system operations. Application denylists may be needed if all acceptable communication sequences cannot be defined, but instead a set of known malicious uses can be denied (e.g., excessive communication attempts, shutdown messages, invalid commands). Devices performing these functions are often referred to as deep-packet inspection (DPI) firewalls, context-aware firewalls, or firewalls blocking specific automation/SCADA protocol aware firewalls. (Citation: Centre for the Protection of National Infrastructure February 2005) | https://attack.mitre.org/mitigations/M0937 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0
M0804 | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | Human User Authentication | Require user authentication before allowing access to data or accepting commands to a device. While strong multi-factor authentication is preferable, it is not always feasible within ICS environments. Performing strong user authentication also requires additional security controls and processes which are often the target of related adversarial techniques (e.g., Valid Accounts, Default Credentials). Therefore, associated ATT&CK mitigations should be considered in addition to this, including [Multi-factor Authentication](https://attack.mitre.org/mitigations/M0932), [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), [User Account Management](https://attack.mitre.org/mitigations/M0918), [Privileged Account Management](https://attack.mitre.org/mitigations/M0926), and [User Account Control](https://attack.mitre.org/mitigations/M1052). | https://attack.mitre.org/mitigations/M0804 | 11 September 2020 | 20 October 2023 | ics-attack | 1.1
M0935 | course-of-action--49b306c1-a046-42c5-a4d2-30f264ada110 | Limit Access to Resource Over Network | Prevent access to file shares, remote access to systems, unnecessary services. Mechanisms to limit access may include use of network concentrators, RDP gateways, etc. | https://attack.mitre.org/mitigations/M0935 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0
M0934 | course-of-action--9e3adcad-0b8f-4ecc-a2f3-06f607f53bf0 | Limit Hardware Installation | Block users or groups from installing or using unapproved hardware on systems, including USB devices. | https://attack.mitre.org/mitigations/M0934 | 11 June 2019 | 19 September 2023 | ics-attack | 1.0
M0805 | course-of-action--8bc4a54e-810c-4600-8b6c-08fa8413a401 | Mechanical Protection Layers | Utilize a layered protection design based on physical or mechanical protection systems to prevent damage to property, equipment, human safety, or the environment. Examples include interlocks, rupture disk, release values, etc. (Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004) | https://attack.mitre.org/mitigations/M0805 | 11 September 2020 | 24 October 2022 | ics-attack | 1.0 | (Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004)
M0806 | course-of-action--fce6866f-9a87-4d3e-a73c-f02d8937fe0e | Minimize Wireless Signal Propagation | Wireless signals frequently propagate outside of organizational boundaries, which provide opportunities for adversaries to monitor or gain unauthorized access to the wireless network. (Citation: CISA March 2010) To minimize this threat, organizations should implement measures to detect, understand, and reduce unnecessary RF propagation. (Citation: DHS National Urban Security Technology Laboratory April 2019) | https://attack.mitre.org/mitigations/M0806 | 11 September 2020 | 19 September 2023 | ics-attack | 1.0 | (Citation: DHS National Urban Security Technology Laboratory April 2019)
M0816 | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | Mitigation Limited or Not Effective | This type of attack technique cannot be easily mitigated with preventative controls since it is based on the abuse of system features. | https://attack.mitre.org/mitigations/M0816 | 11 September 2020 | 24 October 2022 | ics-attack | 1.0
M0932 | course-of-action--ddf3e568-f065-49e2-9106-42029a28ddbd | Multi-factor Authentication | Use two or more pieces of evidence to authenticate to a system; such as username and password in addition to a token from a physical smart card or token generator. Within industrial control environments assets such as low-level controllers, workstations, and HMIs have real-time operational control and safety requirements which may restrict the use of multi-factor. | https://attack.mitre.org/mitigations/M0932 | 10 June 2019 | 19 September 2023 | ics-attack | 1.0
M0807 | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | Network Allowlists | Network allowlists can be implemented through either host-based files or system hosts files to specify what connections (e.g., IP address, MAC address, port, protocol) can be made from a device. Allowlist techniques that operate at the application layer (e.g., DNP3, Modbus, HTTP) are addressed in [Filter Network Traffic](https://attack.mitre.org/mitigations/M0937) mitigation. | https://attack.mitre.org/mitigations/M0807 | 10 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Department of Homeland Security September 2016)
M0931 | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | Network Intrusion Prevention | Use intrusion detection signatures to block traffic at network boundaries. In industrial control environments, network intrusion prevention should be configured so it will not disrupt protocols and communications responsible for real-time functions related to control or safety. | https://attack.mitre.org/mitigations/M0931 | 10 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014)
M0930 | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | Network Segmentation | Architect sections of the network to isolate critical systems, functions, or resources. Use physical and logical segmentation to prevent access to potentially sensitive systems and information. Use a DMZ to contain any internet-facing services that should not be exposed from the internal network. Restrict network access to only required systems and services. In addition, prevent systems from other networks or business functions (e.g., enterprise) from accessing critical process control systems. For example, in IEC 62443, systems within the same secure level should be grouped into a zone, and access to that zone is restricted by a conduit, or mechanism to restrict data flows between zones by segmenting the network. (Citation: IEC February 2019) (Citation: IEC August 2013) | https://attack.mitre.org/mitigations/M0930 | 10 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Dwight Anderson 2014),(Citation: Karen Scarfone; Paul Hoffman September 2009),(Citation: N/A),(Citation: North America Transmission Forum December 2019),(Citation: Keith Stouffer May 2015),(Citation: Department of Homeland Security September 2016)
M0928 | course-of-action--9a945a29-5233-4422-a9e3-3e957b0e8bce | Operating System Configuration | Make configuration changes related to the operating system or a common feature of the operating system that result in system hardening against techniques. | https://attack.mitre.org/mitigations/M0928 | 06 June 2019 | 19 September 2023 | ics-attack | 1.0
M0809 | course-of-action--99c746d7-a08a-4169-94f9-b8c0dad716fa | Operational Information Confidentiality | Deploy mechanisms to protect the confidentiality of information related to operational processes, facility locations, device configurations, programs, or databases that may have information that can be used to infer organizational trade-secrets, recipes, and other intellectual property (IP). | https://attack.mitre.org/mitigations/M0809 | 06 June 2019 | 30 March 2023 | ics-attack | 1.0
M0810 | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | Out-of-Band Communications Channel | Have alternative methods to support communication requirements during communication failures and data integrity attacks. (Citation: National Institute of Standards and Technology April 2013) (Citation: Defense Advanced Research Projects Agency) | https://attack.mitre.org/mitigations/M0810 | 06 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: National Institute of Standards and Technology April 2013)
M0927 | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | Password Policies | Set and enforce secure password policies for accounts. | https://attack.mitre.org/mitigations/M0927 | 06 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: CISA June 2013)
M0926 | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | Privileged Account Management | Manage the creation, modification, use, and permissions associated to privileged accounts, including SYSTEM and root. | https://attack.mitre.org/mitigations/M0926 | 06 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: Microsoft August 2018),(Citation: Microsoft February 2019),(Citation: National Institute of Standards and Technology April 2013),(Citation: Keith Stouffer May 2015),(Citation: Microsoft May 2017)
M0811 | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | Redundancy of Service | Redundancy could be provided for both critical ICS devices and services, such as back-up devices or hot-standbys. | https://attack.mitre.org/mitigations/M0811 | 06 June 2019 | 19 September 2023 | ics-attack | 1.0 | (Citation: M. Rentschler and H. Heine)
M0922 | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | Restrict File and Directory Permissions | Restrict access by setting directory and file permissions that are not specific to users or privileged accounts. | https://attack.mitre.org/mitigations/M0922 | 06 June 2019 | 20 September 2023 | ics-attack | 1.0 | (Citation: Keith Stouffer May 2015),(Citation: National Institute of Standards and Technology April 2013)
M0944 | course-of-action--2ab9fc6d-3cf6-4d7b-85f1-3ad6949233b3 | Restrict Library Loading | Prevent abuse of library loading mechanisms in the operating system and software to load untrusted code by configuring appropriate library loading mechanisms and investigating potential vulnerable software. | https://attack.mitre.org/mitigations/M0944 | 11 June 2019 | 20 September 2023 | ics-attack | 1.0
M0924 | course-of-action--3222a807-521b-4a1a-aa13-f1cda45734b3 | Restrict Registry Permissions | Restrict the ability to modify certain hives or keys in the Windows Registry. | https://attack.mitre.org/mitigations/M0924 | 06 June 2019 | 20 September 2023 | ics-attack | 1.0
M0921 | course-of-action--143b4398-3222-480a-b6a4-e131bc2d3144 | Restrict Web-Based Content | Restrict use of certain websites, block downloads/attachments, block Javascript, restrict browser extensions, etc. | https://attack.mitre.org/mitigations/M0921 | 06 June 2019 | 20 September 2023 | ics-attack | 1.0
M0920 | course-of-action--6a02e38a-9629-40c0-8c7d-e98e3470315c | SSL/TLS Inspection | Break and inspect SSL/TLS sessions to look at encrypted web traffic for adversary activity. | https://attack.mitre.org/mitigations/M0920 | 06 June 2019 | 24 October 2022 | ics-attack | 1.0
M0812 | course-of-action--da44255d-85c5-492c-baf3-ee823d44f848 | Safety Instrumented Systems | Utilize Safety Instrumented Systems (SIS) to provide an additional layer of protection to hazard scenarios that may cause property damage. A SIS will typically include sensors, logic solvers, and a final control element that can be used to automatically respond to an hazardous condition (Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004) . Ensure that all SISs are segmented from operational networks to prevent them from being targeted by additional adversarial behavior. | https://attack.mitre.org/mitigations/M0812 | 06 June 2019 | 24 October 2022 | ics-attack | 1.0
M0954 | course-of-action--facb8840-ebe7-49f1-b464-8ef6c8131e21 | Software Configuration | Implement configuration changes to software (other than the operating system) to mitigate security risks associated with how the software operates. | https://attack.mitre.org/mitigations/M0954 | 19 July 2019 | 20 September 2023 | ics-attack | 1.0
M0813 | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | Software Process and Device Authentication | Require the authentication of devices and software processes where appropriate. Devices that connect remotely to other systems should require strong authentication to prevent spoofing of communications. Furthermore, software processes should also require authentication when accessing APIs. | https://attack.mitre.org/mitigations/M0813 | 06 June 2019 | 20 September 2023 | ics-attack | 1.0
M0814 | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | Static Network Configuration | Configure hosts and devices to use static network configurations when possible, protocols that require dynamic discovery/addressing (e.g., ARP, DHCP, DNS) can be used to manipulate network message forwarding and enable various AiTM attacks. This mitigation may not always be usable due to limited device features or challenges introduced with different network configurations. | https://attack.mitre.org/mitigations/M0814 | 06 June 2019 | 20 September 2023 | ics-attack | 1.1 | (Citation: D. Parsons and D. Wylie September 2019),(Citation: Langner November 2018),(Citation: Josh Rinaldi April 2016),(Citation: Colin Gray),(Citation: Aditya K Sood July 2019)
M0817 | course-of-action--ac8f3492-7fbb-4a0a-b0b4-b75ec676136c | Supply Chain Management | Implement a supply chain management program, including policies and procedures to ensure all devices and components originate from a trusted supplier and are tested to verify their integrity. | https://attack.mitre.org/mitigations/M0817 | 12 April 2021 | 20 September 2023 | ics-attack | 1.0 | (Citation: Robert A. Martin January 2021)
M0919 | course-of-action--d48b79b2-076d-483e-949c-0d38aa347499 | Threat Intelligence Program | A threat intelligence program helps an organization generate their own threat intelligence information and track trends to inform defensive priorities to mitigate risk. | https://attack.mitre.org/mitigations/M0919 | 06 June 2019 | 24 October 2022 | ics-attack | 1.0
M0951 | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | Update Software | Perform regular software updates to mitigate exploitation risk. Software updates may need to be scheduled around operational down times. | https://attack.mitre.org/mitigations/M0951 | 11 June 2019 | 20 September 2023 | ics-attack | 1.0
M0918 | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | User Account Management | Manage the creation, modification, use, and permissions associated to user accounts. | https://attack.mitre.org/mitigations/M0918 | 06 June 2019 | 20 September 2023 | ics-attack | 1.0
M0917 | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | User Training | Train users to be aware of access or manipulation attempts by an adversary to reduce the risk of successful spearphishing, social engineering, and other techniques that involve user interaction. | https://attack.mitre.org/mitigations/M0917 | 06 June 2019 | 20 September 2023 | ics-attack | 1.0
M0818 | course-of-action--1cbcceef-3233-4062-aa86-ec91afe39517 | Validate Program Inputs | Devices and programs designed to interact with control system parameters should validate the format and content of all user inputs and actions to ensure the values are within intended operational ranges. These values should be evaluated and further enforced through the program logic running on the field controller. If a problematic or invalid input is identified, the programs should either utilize a predetermined safe value or enter a known safe state, while also logging or alerting on the event.(Citation: PLCTop20 Mar 2023) | https://attack.mitre.org/mitigations/M0818 | 22 March 2023 | 20 September 2023 | ics-attack | 1.0 | (Citation: PLCTop20 Mar 2023)
M0916 | course-of-action--de0bc375-50e1-4e26-a342-a8ff8c9d3037 | Vulnerability Scanning | Vulnerability scanning is used to find potentially exploitable software vulnerabilities to remediate them. | https://attack.mitre.org/mitigations/M0916 | 06 June 2019 | 20 September 2023 | ics-attack | 1.0 | (Citation: OWASP)
M0815 | course-of-action--98aa0d61-fc9d-4b2d-8f18-b25d03549f53 | Watchdog Timers | Utilize watchdog timers to ensure devices can quickly detect whether a system is unresponsive. | https://attack.mitre.org/mitigations/M0815 | 06 June 2019 | 30 March 2023 | ics-attack | 1.0

## matrix
Initial Access | Execution | Persistence | Privilege Escalation | Evasion | Discovery | Lateral Movement | Collection | Command and Control | Inhibit Response Function | Impair Process Control | Impact
Drive-by Compromise | Autorun Image | Hardcoded Credentials | Exploitation for Privilege Escalation | Change Operating Mode | Network Connection Enumeration | Default Credentials | Adversary-in-the-Middle | Commonly Used Port | Activate Firmware Update Mode | Brute Force I/O | Damage to Property
Exploit Public-Facing Application | Change Operating Mode | Modify Program | Hooking | Exploitation for Evasion | Network Sniffing | Exploitation of Remote Services | Automated Collection | Connection Proxy | Alarm Suppression | Modify Parameter | Denial of Control
Exploitation of Remote Services | Command-Line Interface | Module Firmware |  | Indicator Removal on Host | Remote System Discovery | Hardcoded Credentials | Data from Information Repositories | Standard Application Layer Protocol | Block Command Message | Module Firmware | Denial of View
External Remote Services | Execution through API | Project File Infection |  | Masquerading | Remote System Information Discovery | Lateral Tool Transfer | Data from Local System |  | Block Reporting Message | Spoof Reporting Message | Loss of Availability
Internet Accessible Device | Graphical User Interface | System Firmware |  | Rootkit | Wireless Sniffing | Program Download | Detect Operating Mode |  | Block Serial COM | Unauthorized Command Message | Loss of Control
Remote Services | Hooking | Valid Accounts |  | Spoof Reporting Message |  | Remote Services | I/O Image |  | Change Credential |  | Loss of Productivity and Revenue
Replication Through Removable Media | Modify Controller Tasking |  |  | System Binary Proxy Execution |  | Valid Accounts | Monitor Process State |  | Data Destruction |  | Loss of Protection
Rogue Master | Native API | [5 empty] | Point & Tag Identification |  | Denial of Service |  | Loss of Safety
Spearphishing Attachment | Scripting | [5 empty] | Program Upload |  | Device Restart/Shutdown |  | Loss of View
Supply Chain Compromise | User Execution | [5 empty] | Screen Capture |  | Manipulate I/O Image |  | Manipulation of Control
Transient Cyber Asset | [6 empty] | Wireless Sniffing |  | Modify Alarm Settings |  | Manipulation of View
Wireless Compromise | [8 empty] | Rootkit |  | Theft of Operational Information
Service Stop
System Firmware

## relationships
source ID | source name | source ref | source type | mapping type | target ID | target name | target ref | target type | mapping description | STIX ID | created | last modified
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | attributed-to | G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | (Citation: Andy Greenberg June 2017) (Citation: US District Court Indictment GRU Unit 74455 October 2020) | relationship--4d407dda-944a-4974-b1c2-0a04d2c9ee4c | 27 September 2023 | 27 September 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | attributed-to | G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | (Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: Joe Slowik August 2019) | relationship--90647f03-38a4-4364-a3af-53640a81360e | 31 March 2023 | 31 March 2023
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | attributed-to | G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | (Citation: Mandiant-Sandworm-Ukraine-2022)(Citation: Dragos-Sandworm-Ukraine-2022) | relationship--d3717846-eaab-4fde-99f6-a972dec9323b | 27 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | attributed-to | G0088 | TEMP.Veles | intrusion-set--9538b1a4-4120-4e2d-bf59-3b11fcab05a4 | group | (Citation: FireEye TEMP.Veles 2018)(Citation: FireEye TRITON Dec 2017) | relationship--538e5653-137a-4ce2-8b08-5ba69caa794a | 25 March 2024 | 25 March 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | attributed-to | G1027 | CyberAv3ngers | intrusion-set--a07a367a-146c-45a8-a830-d3d337b9befa | group | (Citation: CISA AA23-335A IRGC-Affiliated December 2023) | relationship--9a55e351-d3b7-460a-9a9d-6714c00db5f0 | 25 March 2024 | 19 April 2024
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Monitor asset log which may provide information that an asset has been placed into Firmware Update Mode. Some assets may log firmware updates themselves without logging that the device has been placed into update mode. | relationship--d406671b-4d22-4cd5-8568-d04b0b70b51c | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Monitor application logs for changes to settings and other events associated with network protocols and other services commonly abused for AiTM. | relationship--dda29418-9570-405a-b7db-97e951e5aa53 | 26 September 2022 | 14 October 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Monitor application logs for changes to settings and other events associated with network protocols that may be used to block communications. | relationship--86b868be-3e59-4497-9aa9-a2cd951a8f72 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Monitor application logs for changes to settings and other events associated with network protocols that may be used to block communications. | relationship--8baa4d55-c235-44da-b6fe-8866cf7f9915 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Monitor application logs for changes to settings and other events associated with network protocols that may be used to block communications. | relationship--2e377016-bb23-481e-b72b-a2ace8c72eb7 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Some asset application logs may provide information on I/O points related to write commands. Monitor for write commands for an excessive number of I/O points or manipulating a single value an excessive number of times. | relationship--880161a4-d6c9-4e5b-a78d-39319cfa43ab | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Monitor device application logs which may contain information related to operating mode changes, although not all devices produce such logs. | relationship--86c94552-de59-453d-ac06-28a6a64db930 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | Monitor logs from installed applications (e.g., historian logs) for unexpected commands or abuse of system features. | relationship--b064068a-9e17-4ac8-9a92-a1338d7196c7 | 27 September 2022 | 27 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Monitor for third-party application logging, messaging, and/or other artifacts that may leverage information repositories to mine valuable information. Information repositories generally have a considerably large user base, detection of malicious use can be non-trivial. At minimum, access to information repositories performed by privileged users (for example, Active Directory Domain, Enterprise, or Schema Administrators) should be closely monitored and alerted upon, as these types of accounts should generally not be used to access information repositories. If the capability exists, it may be of value to monitor and alert on users that are retrieving and viewing a large number of documents and pages; this behavior may be indicative of programmatic means being used to retrieve all data within the repository. In environments with high-maturity, it may be possible to leverage User-Behavioral Analytics (UBA) platforms to detect and alert on user-based anomalies. | relationship--ce0d3a3a-9c62-4bfb-a47a-7b1b23e9f035 | 11 May 2022 | 30 March 2023
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | Monitor for application logging, messaging, and/or other artifacts that may result from Denial of Service (DoS) attacks which degrade or block the availability of services to users. In addition to network level detections, endpoint logging and instrumentation can be useful for detection. | relationship--7f1e688d-65f7-4737-a4ba-ee482710f8ec | 11 May 2022 | 14 October 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Device restarts and shutdowns may be observable in device application logs. Monitor for unexpected device restarts or shutdowns. | relationship--8dab113a-a713-499b-ba1e-9c2cbeffb3c8 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Firewalls and proxies can inspect URLs for potentially known-bad domains or parameters. They can also do reputation-based analytics on websites and their requested resources such as how old a domain is, who it's registered to, if it's on a known bad list, or how many other users have connected to it before. | relationship--c473686a-2452-4ee6-bf1d-54bf3e575d95 | 11 May 2022 | 14 October 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Detecting software exploitation may be difficult depending on the tools available. Software exploits may not always succeed or may cause the exploited process to become unstable or crash. Web Application Firewalls may detect improper inputs attempting exploitation. | relationship--375b7e67-8b3f-4102-9e3e-7e356b6c8bf4 | 11 May 2022 | 14 October 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Detecting software exploitation may be difficult depending on the tools available. Software exploits may not always succeed or may cause the exploited process to become unstable or crash. | relationship--3dc3aec5-0056-46e8-8073-a7e32d3d929d | 30 September 2022 | 30 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Detecting software exploitation may be difficult depending on the tools available. Software exploits may not always succeed or may cause the exploited process to become unstable or crash. | relationship--9f25cdae-7d0f-49cd-acaf-481f71195ae5 | 27 September 2022 | 27 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Detecting software exploitation may be difficult depending on the tools available. Software exploits may not always succeed or may cause the exploited process to become unstable or crash, which may be recorded in the application log. | relationship--8da928a0-1c87-471f-aad7-5a1fdd438357 | 11 May 2022 | 14 October 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | When authentication is not required to access an exposed remote service, monitor for follow-on activities such as anomalous external use of the exposed API or application. | relationship--e8d5ee60-952f-42ff-bf48-7da9cd0fdb23 | 11 May 2022 | 14 October 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Monitor ICS asset application logs that indicate alarm settings have changed, although not all assets will produce such logs. | relationship--00b98fa6-4913-40a4-8920-befed8621c41 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | Monitor asset application logs for information that indicate task parameters have changed. | relationship--0c4aaf6c-4b72-401f-950b-6d65ceb1267a | 27 September 2022 | 27 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | Monitor device application logs parameter changes, although not all devices will produce such logs. | relationship--97df42a5-e6d3-4fb7-a158-c161d14624ab | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | Monitor device application logs that indicate the program has changed, although not all devices produce such logs. | relationship--d2addaa7-0fdf-44e3-9b20-c63b2b4179af | 27 September 2022 | 27 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Monitor device application logs for firmware changes, although not all devices will produce such logs. | relationship--1d399f67-090e-444b-b75d-eed4b1780f08 | 26 September 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | Monitor applications logs for any access attempts to operational databases (e.g., historians) or other sources of operational data within the ICS environment. These devices should be monitored for adversary collection using techniques relevant to the underlying technologies (e.g., Windows, Linux). | relationship--2683e59a-dee3-485a-a355-ed2ee0a23d5d | 26 September 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Monitor asset application logs which may provide information about requests for points or tags. Look for anomalies related to reading point or tag data, such as new assets using these functions, changes in volume or timing, or unusual information being queried. Many devices provide multiple ways to achieve the same result (e.g., functions with/without an acknowledgment or functions that operate on a single point vs. multiple points). Monitor for changes in the functions used. | relationship--7f3ab726-ca49-4d47-b2b5-6246c6e4fdd3 | 26 September 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Monitor devices configuration logs which may contain alerts that indicate whether a program download has occurred. Devices may maintain application logs that indicate whether a full program download, online edit, or program append function has occurred. | relationship--86ede365-4539-4475-b90b-9b3bfd2dbe97 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Monitor for device alarms produced when program uploads occur, although not all devices will produce such alarms. | relationship--54e73627-95de-4e6e-abf0-d93e20a1fe8f | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Monitor for new master devices communicating with outstation assets, which may be visible in asset application logs. | relationship--f4f98ce1-d0b8-4699-b602-33a6a6ffca67 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Monitor mail server and proxy logs for evidence of messages originating from spoofed addresses, including records indicating failed DKIM+SPF validation or mismatched message headers.(Citation: Microsoft Anti Spoofing)(Citation: ACSC Email Spoofing) Anti-virus can potentially detect malicious documents and attachments as they're scanned to be stored on the email server or on the user's computer. | relationship--c7a1037f-cb28-40d4-be19-78e2f0e0aa68 | 11 May 2022 | 14 October 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Monitor device application logs for firmware changes, although not all devices will produce such logs. | relationship--87eb5825-c918-444f-8da5-67da9eea9906 | 26 September 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Networking devices such as switches may log when new client devices connect (e.g., SNMP notifications). Monitor for any logs documenting changes to network connection status to determine when a new connection has occurred, including the resulting addresses (e.g., IP, MAC) of devices on that network. | relationship--7c2f82ff-bde7-4ab8-b6ab-35d7f7f498dd | 27 September 2022 | 27 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Monitor for anomalous or unexpected commands that may result in changes to the process operation (e.g., discrete write, logic and device configuration, mode changes) observable via asset application logs. | relationship--37abb3d5-24fc-4397-844e-07548d324729 | 11 May 2022 | 26 September 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Monitor for application logging, messaging, and/or other artifacts that may rely upon specific actions by a user in order to gain execution. | relationship--3c341d13-938e-4535-ac75-10a79abc7017 | 11 May 2022 | 14 October 2022
| Application Log Content | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | datacomponent | detects | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Monitor application logs for new or unexpected devices or sessions on wireless networks. | relationship--cfcbca89-8912-40c0-ac15-47882162b132 | 11 May 2022 | 26 September 2022
| Asset Inventory | x-mitre-data-component--b05a614b-033c-4578-b4f2-c63a9feee706 | datacomponent | detects | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Consult asset management systems to understand expected alarm settings. | relationship--4b57e41c-246f-44b3-b259-1811d5275e10 | 26 September 2022 | 26 September 2022
| Asset Inventory | x-mitre-data-component--b05a614b-033c-4578-b4f2-c63a9feee706 | datacomponent | detects | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | Monitor asset management systems for device configuration changes which can be used to understand expected parameter settings. | relationship--77821dbb-367e-455f-bcae-b87412e88f1b | 26 September 2022 | 26 September 2022
| Asset Inventory | x-mitre-data-component--b05a614b-033c-4578-b4f2-c63a9feee706 | datacomponent | detects | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Consult asset management systems to understand expected program versions. | relationship--81117328-e2bb-431c-a1ca-6ba7e6816637 | 26 September 2022 | 26 September 2022
| Asset Inventory | x-mitre-data-component--b05a614b-033c-4578-b4f2-c63a9feee706 | datacomponent | detects | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Consult asset management systems which may help with the detection of computer systems or network devices that should not exist on a network. | relationship--1fe3e5fc-7dd6-4e14-b9da-edb1a2aae459 | 23 September 2022 | 26 September 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Monitor executed commands and arguments for actions that could be taken to collect internal data. | relationship--7e87ce08-a428-4e55-876e-80d2760121a5 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | On Windows and Unix systems monitor executed commands and arguments that may use shell commands for execution. Shells may be common on administrator, developer, or power user systems depending on job function. On network device and embedded system CLIs consider reviewing command history if unauthorized or suspicious commands were used to modify device configuration. | relationship--a28ecd81-a7dd-404c-9d7b-ce670b0fc83b | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Monitor executed commands and arguments for binaries that could be involved in data destruction activity, such as SDelete. | relationship--fb80368e-b3f6-4fa3-828b-b1cf792ea161 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Monitor executed commands and arguments that may search and collect local system sources, such as file systems or local databases, to find files of interest and sensitive data. Remote access tools with built-in features may interact directly with the Windows API to gather data. Data may also be acquired through Windows system management tools such as [Windows Management Instrumentation](https://attack.mitre.org/techniques/T1047) and [PowerShell](https://attack.mitre.org/techniques/T1059/001). | relationship--aaacfa83-033f-4555-ba6b-ecc7692a25aa | 30 March 2023 | 30 March 2023
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | Monitor executed commands and arguments related to services specifically designed to accept remote graphical connections, such as RDP and VNC. [Remote Services](https://attack.mitre.org/techniques/T0886) and [Valid Accounts](https://attack.mitre.org/techniques/T0859) may be used to access a host’s GUI. | relationship--6902da63-3b59-46f3-99e0-6008dd47ab70 | 27 September 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Monitor executed commands and arguments that may delete or alter generated artifacts on a host system, including logs or captured files such as quarantined malware. | relationship--3f5f9f9d-9bb3-4461-b85b-501f6077e7b8 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Monitor executed commands and arguments for abnormal usage of utilities and command-line arguments that may be used in support of remote transfer of files. | relationship--7c329018-b591-42c4-8806-4d02ccd47476 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Monitor executed commands and arguments that may attempt to manipulate features of their artifacts to make them appear legitimate or benign to users and/or security tools.(Citation: Twitter ItsReallyNick Masquerading Update) | relationship--73a48431-3597-4a72-acb8-c1e5019073e2 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | Monitor executed commands and arguments that may look for details about the network configuration and settings, such as IP and/or MAC addresses, of systems they access or through information discovery of remote systems. Also monitor executed commands and arguments that may attempt to get a listing of network connections to or from the compromised system they are currently accessing or from remote systems by querying for information over the network. Information may also be acquired through Windows system management tools such as [Windows Management Instrumentation](https://attack.mitre.org/techniques/T1047) and [PowerShell](https://attack.mitre.org/techniques/T1059/001). | relationship--0b7f643e-8975-4998-acbb-7405fa944a68 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Monitor executed commands and arguments for actions that aid in sniffing network traffic to capture information about an environment. | relationship--e5b62475-bd08-4ac6-a6f7-78f1843bf506 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Monitor executed commands and arguments to services specifically designed to accept remote connections, such as RDP, Telnet, SSH, and VNC. The adversary may then perform these actions using [Valid Accounts](https://attack.mitre.org/techniques/T0859). | relationship--7d66eae7-0dd4-4d21-ab07-8f7e350a7105 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | Monitor executed commands and arguments that may attempt to take screen captures of the desktop to gather information over the course of an operation. | relationship--13fb2612-7c23-4b9d-a6e1-76f78062fc52 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Monitor command-line arguments for script execution and subsequent behavior. Actions may be related to network and system information Discovery, Collection, or other scriptable post-compromise behaviors and could be used as indicators of detection leading back to the source script. Scripts are likely to perform actions with various effects on a system that may generate events, depending on the types of monitoring used. | relationship--15a39e3b-124e-4e68-95b5-7b8020225c12 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Monitor executed commands and arguments that may stop or disable services on a system to render those services unavailable to legitimate users. | relationship--214eb531-411c-4b90-9dbf-dc0183cbb919 | 11 May 2022 | 14 October 2022
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | Monitor executed commands and associated arguments for application programs which support executing custom code, scripts, commands, or executables. | relationship--6e7e6dfa-99ed-4cf1-b836-16ad0ae0924b | 25 March 2024 | 25 March 2024
| Command Execution | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | datacomponent | detects | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Monitor for newly executed processes that depend on user interaction, especially for applications that can embed programmatic capabilities (e.g., Microsoft Office products with scripts, installers, zip files). This includes compression applications, such as those for zip files, that can be used to [Deobfuscate/Decode Files or Information](https://attack.mitre.org/techniques/T1140) in payloads. For added context on adversary procedures and background see [User Execution](https://attack.mitre.org/techniques/T1204) and applicable sub-techniques. | relationship--3663f10d-4a2c-4d37-bf5f-337c9891c2f4 | 11 May 2022 | 27 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Monitor device alarms that indicate the devices has been placed into Firmware Update Mode, although not all devices produce such alarms. | relationship--655e2f91-5d43-4c47-b7e0-8248b351f3ba | 11 May 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Monitor for loss of expected device alarms which could indicate alarms are being suppressed. As noted in the technique description, there may be multiple sources of alarms in an ICS environment. Discrepancies between alarms may indicate the adversary is suppressing some but not all the alarms in the environment. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--b182692b-5eb3-4edc-b455-1f92d64b98ec | 26 September 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | Monitor for device alarms produced when device management passwords are changed, although not all devices will produce such alarms. | relationship--6acf3236-d7e6-416c-90e5-5cf6bd89e01d | 30 March 2023 | 30 March 2023
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Monitor alarms for information about when an operating mode is changed, although not all devices produce such logs. | relationship--f145b7e5-048b-46e7-8439-e2b88917523c | 11 May 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Devices may produce alarms about restarts or shutdowns. Monitor for unexpected device restarts or shutdowns. | relationship--aa205915-7571-47ee-8bc6-5aa1ace86690 | 11 May 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | Monitor device alarms that indicate controller task parameters have changed, although not all devices produce such alarms. [Program Download](https://attack.mitre.org/techniques/T0843) may be used to enable this technique. Monitor for program downloads which may be noticeable via operational alarms. Asset management systems should be consulted to understand expected program versions. | relationship--94c903f4-a6c1-40c4-9e9b-0896a5d43b7e | 27 September 2022 | 27 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | Monitor for device alarms produced when parameters are changed, although not all devices will produce such alarms. | relationship--b0fe8a56-cb76-4d79-9ba9-9358ef08aa08 | 11 May 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | Monitor device alarms that indicate the program has changed, although not all devices produce such alarms. | relationship--7912946d-1605-465a-a55c-36bb104235ab | 27 September 2022 | 27 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Monitor for firmware changes which may be observable via operational alarms from devices. | relationship--1377fdf9-5201-4204-b6d3-df2fb5f4d02f | 26 September 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Monitor device alarms for program downloads, although not all devices produce such alarms. | relationship--43777394-ff59-4261-b1cf-b41a1f4f4d8b | 11 May 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Monitor for new master devices communicating with outstations, which may be visible in alarms within the ICS environment. | relationship--aa726ced-f2ac-4113-8d05-8687b7d7ff91 | 26 September 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Monitor asset logs for alarms or other information the adversary is unable to directly suppress. Relevant alarms include those from a loss of communications due to [Adversary-in-the-Middle](https://attack.mitre.org/techniques/T0830) activity. | relationship--21134484-2d59-46b7-b878-527121fff1e3 | 26 September 2022 | 26 September 2022
| Device Alarm | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | datacomponent | detects | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Monitor for firmware changes which may be observable via operational alarms from devices. | relationship--10e87e4b-a231-42e3-a011-0031f8226936 | 26 September 2022 | 26 September 2022
| Drive Creation | x-mitre-data-component--3d6e6b3b-4aa8-40e1-8c47-91db0f313d9f | datacomponent | detects | T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | Monitor for newly constructed drive letters or mount points to removable media. | relationship--e78ff18e-c919-4145-b8b8-540ae7dc94d2 | 26 March 2024 | 26 March 2024
| Drive Creation | x-mitre-data-component--3d6e6b3b-4aa8-40e1-8c47-91db0f313d9f | datacomponent | detects | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Monitor for newly constructed drive letters or mount points to removable media. | relationship--83e5ebce-8d5d-43ca-a47f-ecb50ae8993a | 11 May 2022 | 14 October 2022
| File Access | x-mitre-data-component--235b7491-2d2b-4617-9a52-3c0783680f71 | datacomponent | detects | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Monitor for unexpected files (e.g., .pdf, .docx, .jpg) viewed for collecting internal data. | relationship--bf75ca96-3f9d-413c-a244-888a3fbf0be3 | 11 May 2022 | 14 October 2022
| File Access | x-mitre-data-component--235b7491-2d2b-4617-9a52-3c0783680f71 | datacomponent | detects | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Monitor for unexpected/abnormal access to files that may be malicious collection of local data, such as user files (e.g., .pdf, .docx, .jpg, .dwg ) or local databases. | relationship--052552e9-eac0-4b37-9df8-2e921053e305 | 30 March 2023 | 30 March 2023
| File Access | x-mitre-data-component--235b7491-2d2b-4617-9a52-3c0783680f71 | datacomponent | detects | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | Monitor for files (such as /etc/hosts) being accessed that may attempt to get a listing of other systems by IP address, hostname, or other logical identifier on a network that may be used for Lateral Movement from the current system. | relationship--2e0769d7-088e-45d5-a262-6dbc91a95073 | 11 May 2022 | 14 October 2022
| File Access | x-mitre-data-component--235b7491-2d2b-4617-9a52-3c0783680f71 | datacomponent | detects | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | Monitor for files (such as /etc/hosts) being accessed that may attempt to get a listing of other systems by IP address, hostname, or other logical identifier on a network that may be used for Lateral Movement from the current system. | relationship--9d9cd365-8cfe-403f-8ecb-3c23650c13c3 | 26 September 2022 | 14 October 2022
| File Access | x-mitre-data-component--235b7491-2d2b-4617-9a52-3c0783680f71 | datacomponent | detects | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Monitor for files accessed on removable media, particularly those with executable content. | relationship--a1454196-0d86-49f2-8dcb-61145a16b21e | 26 September 2022 | 14 October 2022
| File Access | x-mitre-data-component--235b7491-2d2b-4617-9a52-3c0783680f71 | datacomponent | detects | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Anti-virus can potentially detect malicious documents and files that are downloaded and executed on the user's computer. Endpoint sensing or network sensing can potentially detect malicious events once the file is opened (such as a Microsoft Word document or PDF reaching out to the internet or spawning PowerShell). | relationship--9d75333b-2542-4899-923f-55dc1e077a51 | 27 September 2022 | 14 October 2022
| File Creation | x-mitre-data-component--2b3bfe19-d59a-460d-93bb-2f546adc2d2c | datacomponent | detects | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Monitor for newly constructed files written to disk through a user visiting a website over the normal course of browsing. | relationship--eb06ac7d-117a-48ab-ae3b-8bfa8f332f60 | 11 May 2022 | 14 October 2022
| File Creation | x-mitre-data-component--2b3bfe19-d59a-460d-93bb-2f546adc2d2c | datacomponent | detects | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Monitor for file creation in conjunction with other techniques (e.g., file transfers using [Remote Services](https://attack.mitre.org/techniques/T0886)). | relationship--5c695f49-6c76-4818-88b6-4db2bf029e43 | 11 May 2022 | 27 September 2022
| File Creation | x-mitre-data-component--2b3bfe19-d59a-460d-93bb-2f546adc2d2c | datacomponent | detects | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Monitor for newly constructed files copied to or from removable media. | relationship--38a3c86b-c9bb-4a65-87c9-55429c68684f | 11 May 2022 | 14 October 2022
| File Creation | x-mitre-data-component--2b3bfe19-d59a-460d-93bb-2f546adc2d2c | datacomponent | detects | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Monitor for newly constructed files from a spearphishing emails with a malicious attachment in an attempt to gain access to victim systems. | relationship--6eaf727c-fec3-4e63-8852-eee27c44d596 | 27 September 2022 | 14 October 2022
| File Deletion | x-mitre-data-component--e905dad2-00d6-477c-97e8-800427abd0e8 | datacomponent | detects | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Monitor for unexpected deletion of files. | relationship--8c1b22bd-7e31-427f-a9c5-085a606212ca | 11 May 2022 | 14 October 2022
| File Deletion | x-mitre-data-component--e905dad2-00d6-477c-97e8-800427abd0e8 | datacomponent | detects | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Monitor for a file that may delete or alter generated artifacts on a host system, including logs or captured files such as quarantined malware. | relationship--9ffc1ecb-09de-4841-a1f6-ebd1f3be7cea | 11 May 2022 | 14 October 2022
| File Metadata | x-mitre-data-component--639e87f3-acb6-448a-9645-258f20da4bc5 | datacomponent | detects | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Monitor for contextual file data that may show signs of deletion or alter generated artifacts on a host system, including logs or captured files such as quarantined malware. | relationship--6be102a8-5d9c-494e-a8ce-7b0a1c86a863 | 11 May 2022 | 14 October 2022
| File Metadata | x-mitre-data-component--639e87f3-acb6-448a-9645-258f20da4bc5 | datacomponent | detects | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Monitor for alike file hashes or characteristics (ex: filename) that are created on multiple hosts. | relationship--1f6b87f3-6749-4caa-98d3-265ebbe0ecbe | 11 May 2022 | 14 October 2022
| File Metadata | x-mitre-data-component--639e87f3-acb6-448a-9645-258f20da4bc5 | datacomponent | detects | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Collect file hashes. Monitor for file names that do not match their expected hash. Perform file monitoring. Files with known names but in unusual locations are suspect. Look for indications of common characters that may indicate an attempt to trick users into misidentifying the file type, such as a space as the last character of a file name or the right-to-left override characters"\u202E", "[U+202E]", and "%E2%80%AE". For added context on adversary procedures and background see [Masquerading](https://attack.mitre.org/techniques/T1036) and applicable sub-techniques. | relationship--e1461f8d-6a16-4526-ac0b-0acd27ae8065 | 11 May 2022 | 14 October 2022
| File Metadata | x-mitre-data-component--639e87f3-acb6-448a-9645-258f20da4bc5 | datacomponent | detects | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | Use verification of distributed binaries through hash checking or other integrity checking mechanisms. Scan downloads for malicious signatures. | relationship--881ef4ba-a480-44de-8ab6-be2cdc87dcce | 27 September 2022 | 14 October 2022
| File Modification | x-mitre-data-component--84572de3-9583-4c73-aabd-06ea88123dd8 | datacomponent | detects | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Monitor for changes made to a large quantity of files for unexpected modifications in both user directories and directories used to store programs and OS components (e.g., C:\Windows\System32). | relationship--2057ec71-a94f-49cc-b348-2eeb44899afd | 11 May 2022 | 14 October 2022
| File Modification | x-mitre-data-component--84572de3-9583-4c73-aabd-06ea88123dd8 | datacomponent | detects | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Monitor for changes made to a file may delete or alter generated artifacts on a host system, including logs or captured files such as quarantined malware. | relationship--a82e9f8a-f81e-407a-b284-e0ae5f055c61 | 11 May 2022 | 14 October 2022
| File Modification | x-mitre-data-component--84572de3-9583-4c73-aabd-06ea88123dd8 | datacomponent | detects | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Monitor for changes made to files outside of an update or patch that may attempt to manipulate features of their artifacts to make them appear legitimate or benign to users and/or security tools. | relationship--1acccbe8-64e1-49ad-87df-215d5c87f050 | 11 May 2022 | 14 October 2022
| File Modification | x-mitre-data-component--84572de3-9583-4c73-aabd-06ea88123dd8 | datacomponent | detects | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | Monitor for unexpected changes to project files, although if the malicious modification occurs in tandem with legitimate changes it will be difficult to isolate the unintended changes by analyzing only file systems modifications. | relationship--5771ce27-7cc7-4144-8c11-c1a6d2ac3e2c | 11 May 2022 | 27 September 2022
| File Modification | x-mitre-data-component--84572de3-9583-4c73-aabd-06ea88123dd8 | datacomponent | detects | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Monitor for changes made to files that may stop or disable services on a system to render those services unavailable to legitimate users. | relationship--1f804c9f-3b65-47eb-89f3-83edd0422fdc | 11 May 2022 | 14 October 2022
| Firmware Modification | x-mitre-data-component--b9d031bb-d150-4fc6-8025-688201bf3ffd | datacomponent | detects | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Monitor firmware for unexpected changes. Asset management systems should be consulted to understand known-good firmware versions. Dump and inspect BIOS images on vulnerable systems and compare against known good images.(Citation: MITRE Copernicus) Analyze differences to determine if malicious changes have occurred. Log attempts to read/write to BIOS and compare against known patching behavior. Likewise, EFI modules can be collected and compared against a known-clean list of EFI executable binaries to detect potentially malicious modules. The CHIPSEC framework can be used for analysis to determine if firmware modifications have been performed.(Citation: McAfee CHIPSEC Blog) (Citation: Github CHIPSEC) (Citation: Intel HackingTeam UEFI Rootkit) | relationship--97641754-f215-4b8f-b0cd-0d3142053c76 | 11 May 2022 | 14 October 2022
| Firmware Modification | x-mitre-data-component--b9d031bb-d150-4fc6-8025-688201bf3ffd | datacomponent | detects | T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | Monitor for changes made to firmware for unexpected modifications to settings and/or data that may be used by rootkits to hide the presence of programs, files, network connections, services, drivers, and other system components. Asset management systems should be consulted to understand known-good firmware versions and configurations. | relationship--8b136d10-1fd7-4cd4-a3a7-b648b23adc92 | 11 May 2022 | 14 October 2022
| Firmware Modification | x-mitre-data-component--b9d031bb-d150-4fc6-8025-688201bf3ffd | datacomponent | detects | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Monitor firmware for unexpected changes. Asset management systems should be consulted to understand known-good firmware versions. Dump and inspect BIOS images on vulnerable systems and compare against known good images.(Citation: MITRE Copernicus) Analyze differences to determine if malicious changes have occurred. Log attempts to read/write to BIOS and compare against known patching behavior. Likewise, EFI modules can be collected and compared against a known-clean list of EFI executable binaries to detect potentially malicious modules. The CHIPSEC framework can be used for analysis to determine if firmware modifications have been performed.(Citation: McAfee CHIPSEC Blog) (Citation: Github CHIPSEC) (Citation: Intel HackingTeam UEFI Rootkit) | relationship--f2e672bb-8c73-4066-94d8-7dfb9a8025a7 | 11 May 2022 | 14 October 2022
| Logon Session Creation | x-mitre-data-component--9ce98c86-8d30-4043-ba54-0784d478d0b5 | datacomponent | detects | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Monitor for newly constructed logon behavior within Microsoft's SharePoint can be configured to report access to certain pages and documents.(Citation: Microsoft SharePoint Logging) Sharepoint audit logging can also be configured to report when a user shares a resource.(Citation: Sharepoint Sharing Events) The user access logging within Atlassian's Confluence can also be configured to report access to certain pages and documents through AccessLogFilter.(Citation: Atlassian Confluence Logging) Additional log storage and analysis infrastructure will likely be required for more robust detection capabilities. | relationship--4cce6bf1-1aa9-483d-a733-d6e52e091419 | 11 May 2022 | 30 March 2023
| Logon Session Creation | x-mitre-data-component--9ce98c86-8d30-4043-ba54-0784d478d0b5 | datacomponent | detects | T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | Monitor logon sessions for default credential use. | relationship--98b229f8-6020-4fbb-b104-54fd478c14d9 | 11 May 2022 | 26 September 2022
| Logon Session Creation | x-mitre-data-component--9ce98c86-8d30-4043-ba54-0784d478d0b5 | datacomponent | detects | T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | Monitor for user accounts logged into systems they would not normally access or abnormal access patterns, such as multiple systems over a relatively short period of time. Correlate use of login activity related to remote services with unusual behavior or other malicious or suspicious activity. [Remote Services](https://attack.mitre.org/techniques/T0886) may be used to access a host’s GUI. | relationship--d90b1271-a90d-41c7-9df7-bec47880c82e | 27 September 2022 | 27 September 2022
| Logon Session Creation | x-mitre-data-component--9ce98c86-8d30-4043-ba54-0784d478d0b5 | datacomponent | detects | T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | Monitor logon sessions for hardcoded credential use, when feasible. | relationship--a7fb3abd-c800-408e-8329-2a4f6256ea4a | 29 September 2022 | 29 September 2022
| Logon Session Creation | x-mitre-data-component--9ce98c86-8d30-4043-ba54-0784d478d0b5 | datacomponent | detects | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Monitor for user accounts logged into systems they would not normally access or abnormal access patterns, such as multiple systems over a relatively short period of time. Correlate use of login activity related to remote services with unusual behavior or other malicious or suspicious activity. Adversaries will likely need to learn about an environment and the relationships between systems through Discovery techniques prior to attempting Lateral Movement. For added context on adversary procedures and background see [Remote Services](https://attack.mitre.org/techniques/T1021) and applicable sub-techniques. | relationship--4631bf49-da0b-4415-a226-112c99ff0f64 | 11 May 2022 | 26 September 2022
| Logon Session Creation | x-mitre-data-component--9ce98c86-8d30-4043-ba54-0784d478d0b5 | datacomponent | detects | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Monitor for logon behavior that may abuse credentials of existing accounts as a means of gaining Lateral Movement or Persistence. Correlate other security systems with login information (e.g., a user has an active login session but has not entered the building or does not have VPN access). | relationship--9ad74496-e164-4068-a0f5-379f507ba864 | 11 May 2022 | 14 October 2022
| Logon Session Creation | x-mitre-data-component--9ce98c86-8d30-4043-ba54-0784d478d0b5 | datacomponent | detects | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Monitor login sessions for new or unexpected devices or sessions on wireless networks. | relationship--b8b1739d-dfa2-44e9-907f-7085e262512f | 11 May 2022 | 26 September 2022
| Logon Session Metadata | x-mitre-data-component--39b9db72-8b48-4595-a18d-db5bbba3091b | datacomponent | detects | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Monitor authentication logs and analyze for unusual access patterns, windows of activity, and access outside of normal business hours, including use of [Valid Accounts](https://attack.mitre.org/techniques/T0859). | relationship--e02565fe-65ff-4b70-8a8d-b0abf6d9a9f4 | 11 May 2022 | 14 October 2022
| Logon Session Metadata | x-mitre-data-component--39b9db72-8b48-4595-a18d-db5bbba3091b | datacomponent | detects | T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | Monitor logon activity for unexpected or unusual access to devices from the Internet. | relationship--3d4ea0e2-9f51-40f9-a22b-8265f696fd83 | 11 May 2022 | 26 September 2022
| Logon Session Metadata | x-mitre-data-component--39b9db72-8b48-4595-a18d-db5bbba3091b | datacomponent | detects | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Monitor for suspicious account behavior across systems that share accounts, either user, admin, or service accounts. Examples: one account logged into multiple systems simultaneously; multiple accounts logged into the same machine simultaneously; accounts logged in at odd times or outside of business hours. Activity may be from interactive login sessions or process ownership from accounts being used to execute binaries on a remote system as a particular account. | relationship--c43fbdc0-4c1d-4ff8-9dd2-fd45199dcfaa | 27 September 2022 | 14 October 2022
| Module Load | x-mitre-data-component--c0a4a086-cc20-4e1e-b7cb-29d99dfa3fb1 | datacomponent | detects | T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | Monitor DLL file events, specifically creation of these binary files as well as the loading of DLLs into processes associated with remote graphical connections, such as RDP and VNC. [Remote Services](https://attack.mitre.org/techniques/T0886) may be used to access a host’s GUI. | relationship--ccab2b58-7c47-45fe-bdd3-3444fb53760c | 27 September 2022 | 27 September 2022
| Module Load | x-mitre-data-component--c0a4a086-cc20-4e1e-b7cb-29d99dfa3fb1 | datacomponent | detects | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Monitor DLL file events, specifically creation of these files as well as the loading of DLLs into processes specifically designed to accept remote connections, such as RDP, Telnet, SSH, and VNC. | relationship--3e956d93-e011-40de-ab1b-3f32fa73ae41 | 26 September 2022 | 14 October 2022
| Module Load | x-mitre-data-component--c0a4a086-cc20-4e1e-b7cb-29d99dfa3fb1 | datacomponent | detects | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Monitor for events associated with scripting execution, such as the loading of modules associated with scripting languages (e.g., JScript.dll, vbscript.dll). | relationship--92ea1c2a-3835-43de-bb56-24e937a6f322 | 11 May 2022 | 14 October 2022
| Network Connection Creation | x-mitre-data-component--181a9f8c-c780-4f1f-91a8-edb770e904ba | datacomponent | detects | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Monitor for newly constructed network connections to untrusted hosts that are used to send or receive data. | relationship--fd856176-396c-4121-9754-35e49bfa5758 | 11 May 2022 | 14 October 2022
| Network Connection Creation | x-mitre-data-component--181a9f8c-c780-4f1f-91a8-edb770e904ba | datacomponent | detects | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Monitor for newly constructed network connections into a service specifically designed to accept remote connections, such as RDP, Telnet, SSH, and VNC. Monitor network connections involving common remote management protocols, such as ports tcp:3283 and tcp:5900, as well as ports tcp:3389 and tcp:22 for remote logins. The adversary may use [Valid Accounts](https://attack.mitre.org/techniques/T0859) to enable remote logins. | relationship--a2142552-6b8d-4751-a3d4-1471420c02fc | 11 May 2022 | 14 October 2022
| Network Connection Creation | x-mitre-data-component--181a9f8c-c780-4f1f-91a8-edb770e904ba | datacomponent | detects | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Monitor for newly constructed web-based network connections that are sent to malicious or suspicious destinations (e.g., destinations attributed to phishing campaigns). Consider correlation with process monitoring and command line to detect anomalous processes execution and command line arguments (e.g., monitor anomalies in use of files that do not normally initiate network connections or unusual connections initiated by regsvr32.exe, rundll.exe, SCF, HTA, MSI, DLLs, or msiexec.exe). | relationship--79fccaf1-3592-4af0-8a47-1d325b9fd5a4 | 11 May 2022 | 14 October 2022
| Network Share Access | x-mitre-data-component--f5468e67-51c7-4756-9b4f-65707708e7fa | datacomponent | detects | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | In the case of detecting collection from shared network drives monitor for unexpected and abnormal accesses to network shares. | relationship--9d4be020-4ab0-4f10-9a20-ae8a2886038f | 27 September 2022 | 30 March 2023
| Network Share Access | x-mitre-data-component--f5468e67-51c7-4756-9b4f-65707708e7fa | datacomponent | detects | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Monitor for unexpected network share access, such as files transferred between shares within a network using protocols such as Server Message Block (SMB). | relationship--03ad6a9a-4443-4e33-a7a5-933e22f2e022 | 27 September 2022 | 14 October 2022
| Network Share Access | x-mitre-data-component--f5468e67-51c7-4756-9b4f-65707708e7fa | datacomponent | detects | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Monitor interactions with network shares, such as reads or file transfers, using remote services such as Server Message Block (SMB). For added context on adversary procedures and background see [Remote Services](https://attack.mitre.org/techniques/T1021) and applicable sub-techniques. | relationship--a731ad54-0c3c-47bb-9559-d99950782beb | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Monitor ICS automation network protocols for information that an asset has been placed into Firmware Update Mode. | relationship--154de746-5ea2-43b4-97b2-221b2433cbde | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Monitor network traffic for anomalies associated with known AiTM behavior. For Collection activity where transmitted data is not manipulated, anomalies may be present in network management protocols (e.g., ARP, DHCP). | relationship--ad77a940-150c-4d73-bf5a-1df2d9436f9c | 11 May 2022 | 14 October 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Monitor for information collection on assets that may indicate deviations from standard operational tools. Examples include unexpected industrial automation protocol functions, new high volume communication sessions, or broad collection across many hosts within the network. | relationship--f664bf42-5fb2-41e5-b790-978ddf866da3 | 11 May 2022 | 27 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Monitor network traffic for ICS functions related to write commands for an excessive number of I/O points or manipulating a single value an excessive number of times. | relationship--f8cf3800-6521-41d9-b272-d6ba2db0ccd2 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | Monitor for device credential changes observable in automation or management network protocols. | relationship--f3810d69-0eff-4d62-bdf1-2870cf676bba | 30 March 2023 | 30 March 2023
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Monitor ICS management protocols for functions that change an asset’s operating mode. | relationship--0d305450-d5ca-46fe-8583-36c983dd0a88 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | Monitor for mismatches between protocols and their expected ports (e.g., non-HTTP traffic on tcp:80). Analyze packet contents to detect communications that do not follow the expected protocol behavior for the port that is being used.(Citation: University of Birmingham C2) | relationship--42508a8e-44d5-4af1-9e66-bace5fc94734 | 27 September 2022 | 27 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | Monitor and analyze traffic patterns and packet inspection associated to protocol(s) that do not follow the expected protocol standards and traffic flows (e.g., extraneous packets that do not belong to established flows, gratuitous or anomalous traffic patterns, anomalous syntax, or structure). Consider correlation with process monitoring and command line to detect anomalous processes execution and command line arguments associated to traffic patterns (e.g., monitor anomalies in use of files that do not normally initiate connections for respective protocol(s)). | relationship--08a4f730-bc3f-4050-973f-1ef2847db4e7 | 11 May 2022 | 14 October 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | Monitor network traffic for default credential use in protocols that allow unencrypted authentication. | relationship--711f17c2-c9f6-4d8d-bf79-117fcdc592c0 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | Monitor and analyze traffic patterns and packet inspection associated to protocol(s) that do not follow the expected protocol standards and traffic flows (e.g., extraneous packets that do not belong to established flows, gratuitous or anomalous traffic patterns, anomalous syntax, or structure). Consider correlation with process monitoring and command line to detect anomalous processes execution and command line arguments associated to traffic patterns (e.g., monitor anomalies in use of files that do not normally initiate connections for respective protocol(s)). | relationship--3d20dad6-fb53-4d74-bc7e-54b9b88e1529 | 11 May 2022 | 14 October 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Monitor ICS automation network protocols for functions related to reading an asset’s operating mode. In some cases, there may be multiple ways to detect a device’s operating mode, one of which is typically used in the operational environment. Monitor for the operating mode being checked in unexpected ways. | relationship--78972893-5d8c-480f-a05d-481adc0c8bb0 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Monitor ICS automation protocols for functions that restart or shutdown a device. Commands to restart or shutdown devices may also be observable in traditional IT management protocols. | relationship--ea5828bb-5da7-4ed8-83b8-8d3b0e51cb3a | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Monitor for unusual network traffic that may indicate additional tools transferred to the system. Use network intrusion detection systems, sometimes with SSL/TLS inspection, to look for known malicious scripts (recon, heap spray, and browser identification scripts have been frequently reused), common script obfuscation, and exploit code. | relationship--b778b3c3-5dd3-4c0b-b7d9-78e6bb40a544 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Use deep packet inspection to look for artifacts of common exploit traffic, such as known payloads. | relationship--b0f137d8-3c56-4f6c-9d59-1ec231d61391 | 11 May 2022 | 14 October 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Use deep packet inspection to look for artifacts of common exploit traffic, such as known payloads. | relationship--ee1a52bc-6c1b-4e2c-b296-173dccbc020a | 11 May 2022 | 14 October 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | Monitor network traffic for hardcoded credential use in protocols that allow unencrypted authentication. | relationship--6be3917c-aad7-4a3f-bea2-23e4ba4310ee | 29 September 2022 | 29 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | Monitor for unusual logins to Internet connected devices or unexpected protocols to/from the Internet. Network traffic content will provide valuable context and details about the content of network flows. | relationship--df95c619-33ee-4484-934a-78857717323e | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Monitor for unusual processes with internal network connections creating files on-system which may be suspicious. | relationship--75a60046-c4d7-498a-b256-9a93b5992dcc | 11 May 2022 | 14 October 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Monitor for alarm setting changes observable in automation or management network protocols. | relationship--a618d7e4-23f0-4b8c-9f09-78d04ea7fc55 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | Monitor ICS management protocols for parameter changes, including for unexpected values, changes far exceeding standard values, or for parameters being changed in an unexpected way (e.g., via a new function, at an unusual time). | relationship--b401f65c-5324-4fc0-8fce-0aa2ebf1f919 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | Monitor device management protocols for functions that modify programs such as online edit and program append events. | relationship--2d07e32d-e9cd-4b19-86ad-4573824d6919 | 27 September 2022 | 27 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Monitor ICS management protocols / file transfer protocols for protocol functions related to firmware changes. | relationship--8985cd3c-1429-4681-ad2e-9b3e46588a44 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | Monitor ICS automation network protocols for functions related to reading an operational process state (e.g., “Read” function codes in protocols like DNP3 or Modbus). In some cases, there may be multiple ways to monitor an operational process’ state, one of which is typically used in the operational environment. Monitor for the operating mode being checked in unexpected ways. | relationship--0d540b53-6a5d-4f56-9dee-47707443b149 | 11 May 2022 | 30 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Monitor ICS automation protocols for anomalies related to reading point or tag data, such as new assets using these functions, changes in volume or timing, or unusual information being queried. Many protocols provide multiple ways to achieve the same result (e.g., functions with/without an acknowledgment or functions that operate on a single point vs. multiple points). Monitor for changes in the functions used. | relationship--69146c10-d3d0-4f69-8164-9c21a1a4e10b | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Monitor for protocol functions related to program download or modification. Program downloads may be observable in ICS automation protocols and remote management protocols. | relationship--70a9010c-6943-4274-b854-50901c3e5a0e | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Program uploads may be observable in ICS management protocols or file transfer protocols. Note when protocol functions related to program uploads occur. In cases where the ICS protocols is not well understood, one option is to examine network traffic for the program files themselves using signature-based tools. | relationship--11ab5b1a-b7b3-43bb-bc19-d65bf4ed89f3 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | Monitor for anomalies related to discovery related ICS functions, including devices that have not previously used these functions or for functions being sent to many outstations. Note that some ICS protocols use broadcast or multicast functionality, which may produce false positives. Also monitor for hosts enumerating network connected resources using non-ICS enterprise protocols. | relationship--db52c1b6-4e48-4e8c-a34c-3ca21b26fe8a | 30 September 2022 | 30 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | Monitor for anomalies related to discovery related ICS functions, including devices that have not previously used these functions or for functions being sent to many outstations. Note that some ICS protocols use broadcast or multicast functionality, which may produce false positives. Also monitor for hosts enumerating network connected resources using non-ICS enterprise protocols. | relationship--7d3ef0e3-560c-4e46-a0b4-dd1efc29e835 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Monitor for unexpected ICS protocol functions from new and existing devices. Monitoring known devices requires ICS function level insight to determine if an unauthorized device is issuing commands (e.g., a historian). | relationship--cf703ecc-e9f5-4d56-94d4-8fda9837e614 | 11 May 2022 | 28 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Monitor network traffic for suspicious email attachments. Consider correlation with process monitoring and command line to detect anomalous processes execution and command line arguments associated to traffic patterns (e.g., monitor anomalies in use of files that do not normally initiate connections for respective protocol(s)). Use web proxies to review content of emails including sender information, headers, and attachments for potentially malicious content. | relationship--7d2db896-3051-483c-bc53-ca21832ee085 | 11 May 2022 | 14 October 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Spoofed reporting messages may be detected by reviewing the content of automation protocols, either through detecting based on expected values or comparing to other out of band process data sources. Spoofed messages may not precisely match legitimate messages which may lead to malformed traffic, although traffic may be malformed for many benign reasons. Monitor reporting messages for changes in how they are constructed. Various techniques enable spoofing a reporting message. Consider monitoring for [Rogue Master](https://attack.mitre.org/techniques/T0848) and [Adversary-in-the-Middle](https://attack.mitre.org/techniques/T0830) activity. | relationship--c63c35c2-a402-4d0d-bf25-f48eb9b379c1 | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | Monitor and analyze traffic patterns and packet inspection associated to protocol(s), leveraging SSL/TLS inspection for encrypted traffic, that do not follow the expected protocol standards and traffic flows (e.g., extraneous packets that do not belong to established flows, gratuitous or anomalous traffic patterns, anomalous syntax, or structure). Consider correlation with process monitoring and command line to detect anomalous processes execution and command line arguments associated to traffic patterns (e.g., monitor anomalies in use of files that do not normally initiate connections for respective protocol(s)). | relationship--b116fcca-e872-4735-b7e2-4e4c8e34621a | 11 May 2022 | 14 October 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Monitor ICS management protocols / file transfer protocols for protocol functions related to firmware changes. | relationship--fc1d3924-3210-4ca6-b3cc-a7a525eab47c | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Monitor for unexpected ICS protocol command functions to controllers from existing master devices (including from new processes) or from new devices. The latter is like detection for [Rogue Master](https://attack.mitre.org/techniques/T0848) but requires ICS function level insight to determine if an unauthorized device is issuing commands (e.g., a historian). Monitoring for unexpected or problematic values below the function level will provide better insights into potentially malicious activity but at the cost of additional false positives depending on the underlying operational process. | relationship--f9625775-662c-425e-9ea0-6cb3f3bf5c3c | 11 May 2022 | 26 September 2022
| Network Traffic Content | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | datacomponent | detects | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Monitor and analyze traffic patterns and packet inspection associated with web-based network connections that are sent to malicious or suspicious destinations (e.g., destinations attributed to phishing campaigns). Consider correlation with process monitoring and command line to detect anomalous processes execution and command line arguments (e.g., monitor anomalies in use of files that do not normally initiate network connections or unusual connections initiated by regsvr32.exe, rundll.exe, SCF, HTA, MSI, DLLs, or msiexec.exe). | relationship--fc6cc5f2-ef5b-4a28-a0b2-a277ee98191d | 11 May 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Monitor for network traffic originating from unknown/unexpected hosts. Local network traffic metadata (such as source MAC addressing) as well as usage of network management protocols such as DHCP may be helpful in identifying hardware. For added context on adversary procedures and background see [Adversary-in-the-Middle](https://attack.mitre.org/techniques/T1557) and applicable sub-techniques. | relationship--76b8bbce-1c65-4337-a4d7-320c594dc29e | 11 May 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Monitor for loss of network traffic which could indicate alarms are being suppressed. A loss of expected communications associated with network protocols used to communicate alarm events or process data could indicate this technique is being used. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--5886d4a1-2d4c-40d5-a689-69c475ab6ee2 | 26 September 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Monitor for a loss of network communications, which may indicate this technique is being used. | relationship--9e8990f9-475b-43fe-91fb-25cc0634f0aa | 11 May 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Monitor for a loss of network communications, which may indicate this technique is being used. | relationship--9e0810a5-ad02-487f-b0a8-bf07decca493 | 11 May 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Monitor for a loss of network communications, which may indicate this technique is being used. | relationship--1299dd2d-4f42-4f5f-876b-bf7dacd17c79 | 11 May 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | Analyze network data for uncommon data flows (e.g., new protocols in use between hosts, unexpected ports in use). Processes utilizing the network that do not normally have network communication or have never been seen before are suspicious. | relationship--1ed4d007-6d30-4d5d-8df9-3800ed56e042 | 11 May 2022 | 27 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | Monitor for known proxy protocols (e.g., SOCKS, Tor, peer-to-peer protocols) and tool usage (e.g., Squid, peer-to-peer software) on the network that are not part of normal operations. Also monitor network data for uncommon data flows. Processes utilizing the network that do not normally have network communication or have never been seen before are suspicious. | relationship--3bff265f-7ab9-4dae-b7a3-a5d9bc586f35 | 11 May 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | Monitor network data for uncommon data flows. Processes utilizing the network that do not normally have network communication or have never been seen before are suspicious. | relationship--6aa080d0-6e25-46e5-91d8-4af11f01ceef | 11 May 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Monitor for a loss of network communications, which may indicate a device has been shutdown or restarted. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--8af89a9b-3e95-45f4-a51d-223b1c82db9c | 26 September 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Monitor for network traffic originating from unknown/unexpected systems. | relationship--b8d484f3-85e7-4208-8ae4-72f0e055a290 | 11 May 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | Monitor for unexpected protocols to/from the Internet. While network traffic content and logon session metadata may directly identify a login event, new Internet-based network flows may also be a reliable indicator of this technique. | relationship--54f6293a-1ccb-4dcb-b85c-9a2a57daddb9 | 11 May 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Monitor for network traffic originating from unknown/unexpected hosts. Local network traffic metadata (such as source MAC addressing) as well as usage of network management protocols such as DHCP may be helpful in identifying hardware. | relationship--fc3d0a84-e7c7-415c-ae47-42bc513e9bf9 | 11 May 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Monitor device communication patterns to identify irregular bulk transfers of data between the embedded ICS asset and other nodes within the network. Note these indicators are dependent on the profile of normal operations and the capabilities of the industrial automation protocols involved (e.g., partial program uploads). | relationship--51ed2f2f-d7e2-4699-b6bf-8da9d0361d59 | 26 September 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Monitor network data for uncommon data flows (e.g., time of day, unusual source/destination address) that may be related to abuse of [Valid Accounts](https://attack.mitre.org/techniques/T0859) to log into a service specifically designed to accept remote connections, such as RDP, Telnet, SSH, and VNC. | relationship--31203165-79d0-42e5-81f1-62150dea2c43 | 11 May 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | Monitor for new ICS protocol connections to existing assets or for device scanning (i.e., a host connecting to many devices) over ICS and enterprise protocols (e.g., ICMP, DCOM, WinRM). For added context on adversary enterprise procedures and background see [Remote System Discovery](https://attack.mitre.org/techniques/T1018). | relationship--e4a11381-8608-4c71-966f-df0cbb834fe0 | 30 September 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | Monitor for new ICS protocol connections to existing assets or for device scanning (i.e., a host connecting to many devices) over ICS and enterprise protocols (e.g., ICMP, DCOM, WinRM). | relationship--1e6da55a-ab6c-4583-9e20-583f82096497 | 26 September 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Monitor for network traffic originating from unknown/unexpected devices or addresses. Local network traffic metadata could be used to identify unexpected connections, including unknown/unexpected source MAC addresses connecting to ports associated with operational protocols. Also, network management protocols such as DHCP and ARP may be helpful in identifying unexpected devices. | relationship--321fc522-bc6b-4975-bee4-9098624d1e8c | 11 May 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Various techniques enable spoofing a reporting message. Consider monitoring for [Rogue Master](https://attack.mitre.org/techniques/T0848) and [Adversary-in-the-Middle](https://attack.mitre.org/techniques/T0830) activity which may precede this technique. | relationship--0dca1f7d-9965-467a-bea5-b8baa7c8b9fc | 26 September 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | Monitor and analyze traffic flows that do not follow the expected protocol standards and traffic flows (e.g., extraneous packets that do not belong to established flows , or gratuitous or anomalous traffic patterns). Consider correlation with process monitoring and command line to detect anomalous processes execution and command line arguments associated to traffic patterns (e.g., monitor anomalies in use of files that do not normally initiate connections for respective protocol(s)). | relationship--6bf14e79-3287-4b9e-b222-9d527530df1e | 11 May 2022 | 14 October 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Monitor for network traffic originating from unknown/unexpected hardware devices. Local network traffic metadata (such as source MAC addressing) may be helpful in identifying transient assets. | relationship--6157408d-1eb3-4445-8d8a-14619458954f | 27 September 2022 | 27 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Monitor for new or unexpected connections to controllers, which could indicate an Unauthorized Command Message being sent via [Rogue Master](https://attack.mitre.org/techniques/T0848). | relationship--c726e8af-9b98-4ce9-b8f4-3e82e59d5374 | 26 September 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | New or irregular network traffic flows may indicate potentially unwanted devices or sessions on wireless networks. In Wi-Fi networks monitor for changes such as rogue access points or low signal strength, indicating a device is further away from the access point then expected and changes in the physical layer signal.(Citation: Nzyme Alerts Intro) (Citation: Wireless Intrusion Detection) Network traffic content will provide important context, such as hardware (e.g., MAC) addresses, user accounts, and types of messages sent. | relationship--de8b8a69-5f08-421a-96f0-2bed5707508d | 11 May 2022 | 26 September 2022
| Network Traffic Flow | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | datacomponent | detects | T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | Purely passive network sniffing cannot be detected effectively. In cases where the adversary interacts with the wireless network (e.g., joining a Wi-Fi network) detection may be possible. Monitor for new or irregular network traffic flows which may indicate potentially unwanted devices or sessions on wireless networks. In Wi-Fi networks monitor for changes such as rogue access points or low signal strength, indicating a device is further away from the access point then expected and changes in the physical layer signal.(Citation: Nzyme Alerts Intro) (Citation: Wireless Intrusion Detection) Network traffic content will provide important context, such as hardware (e.g., MAC) addresses, user accounts, and types of messages sent. | relationship--b4b698a7-b80e-41f6-8ca2-a954270cceb3 | 27 September 2022 | 27 September 2022
| OS API Execution | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | datacomponent | detects | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Monitor for API calls that may search local system sources, such as file systems or local databases, to find files of interest and sensitive data. | relationship--8f0fa80a-7f8c-4c54-9277-a6f69bafd6af | 30 March 2023 | 30 March 2023
| OS API Execution | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | datacomponent | detects | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | Devices that provide user access to the underlying operating system may allow the installation of custom software to monitor OS API execution. Monitoring API calls may generate a significant amount of data and may not be useful for defense unless collected under specific circumstances, since benign use of API functions are common and may be difficult to distinguish from malicious behavior. Correlation of other events with behavior surrounding API function calls using API monitoring will provide additional context to an event that may assist in determining if it is due to malicious behavior. | relationship--72bfda0b-31e9-4958-8d40-6efe816d9989 | 27 September 2022 | 14 October 2022
| OS API Execution | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | datacomponent | detects | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | Monitor for API calls that can be used to install a hook procedure, such as the SetWindowsHookEx and SetWinEventHook functions.(Citation: Microsoft Hook Overview)(Citation: Volatility Detecting Hooks Sept 2012) Also consider analyzing hook chains (which hold pointers to hook procedures for each type of hook) using tools(Citation: Volatility Detecting Hooks Sept 2012)(Citation: PreKageo Winhook Jul 2011)(Citation: Jay GetHooks Sept 2011) or by programmatically examining internal kernel structures.(Citation: Zairon Hooking Dec 2006)(Citation: EyeofRa Detecting Hooking June 2017) | relationship--679d216f-9bf7-428a-8d5b-72a84d6d45ab | 27 September 2022 | 14 October 2022
| OS API Execution | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | datacomponent | detects | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Monitor for API calls that may delete or alter generated artifacts on a host system, including logs or captured files such as quarantined malware. | relationship--5a16cecc-4017-4ce8-97db-01cb66a1528e | 11 May 2022 | 14 October 2022
| OS API Execution | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | datacomponent | detects | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | Devices that provide user access to the underlying operating system may allow the installation of custom software to monitor OS API execution. Monitoring API calls may generate a significant amount of data and may not be useful for defense unless collected under specific circumstances, since benign use of API functions are common and may be difficult to distinguish from malicious behavior. Correlation of other events with behavior surrounding API function calls using API monitoring will provide additional context to an event that may assist in determining if it is due to malicious behavior. | relationship--81add433-49d8-43ec-85d5-f48fe80e56e7 | 11 May 2022 | 14 October 2022
| OS API Execution | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | datacomponent | detects | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | Monitor for API calls (such as GetAdaptersInfo() and GetIpNetTable()) that may gather details about the network configuration and settings, such as IP and/or MAC addresses. Also monitor for API calls that may attempt to get a listing of network connections to or from the compromised system they are currently accessing or from remote systems by querying for information over the network. For added context on adversary procedures and background see [System Network Configuration Discovery](https://attack.mitre.org/techniques/T1016) and [System Network Connections Discovery](https://attack.mitre.org/techniques/T1049). | relationship--7dad75e6-f569-4bb9-ad75-5eda55dff0b1 | 11 May 2022 | 14 October 2022
| OS API Execution | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | datacomponent | detects | T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | Monitoring for screen capture behavior will depend on the method used to obtain data from the operating system and write output files. Detection methods could include collecting information from unusual processes using API calls used to obtain image data, and monitoring for image files written to disk, such as CopyFromScreen, xwd, or screencapture.(Citation: CopyFromScreen .NET)(Citation: Antiquated Mac Malware) The data may need to be correlated with other events to identify malicious activity, depending on the legitimacy of this behavior within a given network environment. | relationship--c11a95c2-6e9d-4d90-b6ab-20227869f2e4 | 11 May 2022 | 14 October 2022
| OS API Execution | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | datacomponent | detects | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Remote access tools with built-in features may interact directly with the Windows API to perform these functions outside of typical system utilities. For example, ChangeServiceConfigW may be used by an adversary to prevent services from starting. For added context on adversary procedures and background see [Service Stop](https://attack.mitre.org/techniques/T1489). | relationship--59c65014-1fee-4c2e-9ece-9883159bbed2 | 11 May 2022 | 27 September 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Host-based implementations of this technique may utilize networking-based system calls or network utility commands (e.g., iptables) to locally intercept traffic. Monitor for relevant process creation events. | relationship--40f63b01-dc59-475d-826a-74f38c6e81b9 | 11 May 2022 | 26 September 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | Monitor for newly executed processes that execute from removable media after it is mounted or when initiated by a user. | relationship--fa726dae-84da-4500-8516-1522da2c6fa4 | 26 March 2024 | 26 March 2024
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | Monitor for processes spawning from known command shell applications (e.g., PowerShell, Bash). Benign activity will need to be allow-listed. This information can be useful in gaining additional insight to adversaries' actions through how they use native processes or custom tools. | relationship--ca0c26d7-c4a9-4c4a-bbd4-f3df4b1f5f69 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Monitor for newly executed processes of binaries that could be involved in data destruction activity, such as SDelete. | relationship--55f3dd59-08be-4e23-a680-b6db7850b399 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Monitor for newly executed processes that may search local system sources, such as file systems or local databases, to find files of interest and sensitive data. | relationship--06782c99-93de-4db9-9c30-6f96aef894d2 | 30 March 2023 | 30 March 2023
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Monitor for behaviors on the endpoint system that might indicate successful compromise, such as abnormal behaviors of browser processes. This could include suspicious files written to disk. | relationship--dadfed22-d70c-482b-9026-964396d75484 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | Monitor for newly executed processes related to services specifically designed to accept remote graphical connections, such as RDP and VNC. [Remote Services](https://attack.mitre.org/techniques/T0886) and [Valid Accounts](https://attack.mitre.org/techniques/T0859) may be used to access a host’s GUI. | relationship--15188683-7ded-4578-9102-73459ecbe095 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Monitor for newly executed processes that may delete or alter generated artifacts on a host system, including logs or captured files such as quarantined malware. | relationship--af24e067-966d-41f8-b1ea-5a6e11ff1a2a | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Monitor newly constructed processes that assist in lateral tool transfers, such as file transfer programs. | relationship--8b491011-322d-4e0b-8f79-449e1b2ee185 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | Monitor for executed processes (such as ipconfig/ifconfig and arp) with arguments that may look for details about the network configuration and settings, such as IP and/or MAC addresses. Also monitor for executed processes that may attempt to get a listing of network connections to or from the compromised system they are currently accessing or from remote systems by querying for information over the network. | relationship--66d637a0-4874-4b12-bd3a-b408acb06d26 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Monitor for newly executed processes that can aid in sniffing network traffic to capture information about an environment. | relationship--892c0bff-17b6-447b-a213-6a3189a1df82 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Monitor for newly executed processes related to services specifically designed to accept remote connections, such as RDP, Telnet, SSH, and VNC. The adversary may use [Valid Accounts](https://attack.mitre.org/techniques/T0859) to login and may perform follow-on actions that spawn additional processes as the user. | relationship--5901e8b3-7df0-43e0-bdc5-f4fd2792a572 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | Monitor for newly executed processes that can be used to discover remote systems, such as ping.exe and tracert.exe , especially when executed in quick succession.(Citation: Elastic - Koadiac Detection with EQL) Consider monitoring for new processes engaging in scanning activity or connecting to multiple systems by correlating process creation network data. | relationship--39963a04-9675-4fa4-87ea-1b34145cc569 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | Monitor for newly executed processes that can be used to discover remote systems, such as ping.exe and tracert.exe, especially when executed in quick succession.(Citation: Elastic - Koadiac Detection with EQL) Consider monitoring for new processes engaging in scanning activity or connecting to multiple systems by correlating process creation network data. | relationship--a7a4b080-e4a6-4c46-b2c7-84119df76393 | 26 September 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Monitor for newly executed processes that execute from removable media after it is mounted or when initiated by a user. If a remote access tool is used in this manner to move laterally, then additional actions are likely to occur after execution, such as opening network connections for Command and Control and system and network information Discovery. | relationship--26254163-4f25-4d30-8456-ca093459ff32 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Monitor log files for process execution through command-line and scripting activities. This information can be useful in gaining additional insight to adversaries' actions through how they use native processes or custom tools. Also monitor for loading of modules associated with specific languages. | relationship--193c3cd3-0b22-4839-a1fa-413aee61e882 | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Monitor for newly executed processes that may stop or disable services on a system to render those services unavailable to legitimate users. | relationship--aae5d42f-6bfc-44b6-8ff3-4b7abb4526ca | 11 May 2022 | 14 October 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Monitor for suspicious descendant process spawning from Microsoft Office and other productivity software.(Citation: Elastic - Koadiac Detection with EQL) For added context on adversary procedures and background see [Spearphishing Attachment](https://attack.mitre.org/techniques/T1566/001). | relationship--06f15629-d050-434a-aed1-3bb3f90c97b2 | 27 September 2022 | 27 September 2022
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | Monitor for unusual processes execution, especially for processes that allow the proxy execution of malicious files. | relationship--b259c196-2a23-4173-9ed5-aae1c948579e | 25 March 2024 | 28 March 2024
| Process Creation | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | datacomponent | detects | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Monitor for newly executed processes that depend on user interaction, especially for applications that can embed programmatic capabilities (e.g., Microsoft Office products with scripts, installers, zip files). This includes compression applications, such as those for zip files, that can be used to [Deobfuscate/Decode Files or Information](https://attack.mitre.org/techniques/T1140) in payloads. | relationship--c664bb6c-59f0-4b31-bbb4-ef66fca933d4 | 11 May 2022 | 14 October 2022
| Process History/Live Data | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | datacomponent | detects | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Monitor for loss of operational process data which could indicate alarms are being suppressed. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--949b498c-ca3f-4704-90bd-a22a4d34067f | 11 May 2022 | 26 September 2022
| Process History/Live Data | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | datacomponent | detects | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Monitor for lack of operational process data which may help identify a loss of communications. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--567acebd-4ba2-4723-a74d-514992321ccc | 11 May 2022 | 26 September 2022
| Process History/Live Data | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | datacomponent | detects | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Monitor for lack of operational process data which may help identify a loss of communications. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--fe22637e-7187-4990-b24a-5dc851eec736 | 11 May 2022 | 26 September 2022
| Process History/Live Data | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | datacomponent | detects | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Monitor for lack of operational process data which may help identify a loss of communications. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--1c12b1d6-d636-45c6-98f4-947ddb502cb0 | 11 May 2022 | 26 September 2022
| Process History/Live Data | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | datacomponent | detects | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Monitor operational process data for write commands for an excessive number of I/O points or manipulating a single value an excessive number of times. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--3c5bc8de-a7a4-4bda-a82f-8d149ec927f1 | 11 May 2022 | 26 September 2022
| Process History/Live Data | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | datacomponent | detects | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | Monitor operational data for indicators of temporary data loss which may indicate a Denial of Service. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--e18af08c-3953-4b1d-b46c-45572fdb5187 | 11 May 2022 | 27 September 2022
| Process History/Live Data | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | datacomponent | detects | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Data about the industrial process may indicate it is operating outside of expected bounds and could help indicate that that an alarm setting has changed. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--97538255-b049-4d15-91c4-6b227cbea476 | 11 May 2022 | 26 September 2022
| Process History/Live Data | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | datacomponent | detects | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Monitor industrial process history data for events that correspond with command message functions, such as setpoint modification or changes to system status for key devices. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--0e275c19-7688-47f8-8cd5-85eaacec465b | 11 May 2022 | 26 September 2022
| Process Metadata | x-mitre-data-component--ee575f4a-2d4f-48f6-b18b-89067760adc1 | datacomponent | detects | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | Verify integrity of live processes by comparing code in memory to that of corresponding static binaries, specifically checking for jumps and other instructions that redirect code flow. | relationship--e09f3308-57d7-4b2b-b340-784b88ae61ca | 27 September 2022 | 14 October 2022
| Process Metadata | x-mitre-data-component--ee575f4a-2d4f-48f6-b18b-89067760adc1 | datacomponent | detects | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Monitor for file names that are mismatched between the file name on disk and that of the binary's metadata. This is a likely indicator that a binary was renamed after it was compiled. For added context on adversary procedures and background see [Masquerading](https://attack.mitre.org/techniques/T1036) and applicable sub-techniques. | relationship--636baf5a-1a1c-476b-bc54-fb27b27b58a2 | 11 May 2022 | 27 September 2022
| Process Metadata | x-mitre-data-component--ee575f4a-2d4f-48f6-b18b-89067760adc1 | datacomponent | detects | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Monitor contextual data about a running process, which may include information such as environment variables, image name, user/owner, or other information that may reveal abuse of system features. | relationship--478cef79-cf4e-4b37-9562-b45cdeb088a4 | 26 September 2022 | 14 October 2022
| Process Termination | x-mitre-data-component--61f1d40e-f3d0-4cc6-aa2d-937b6204194f | datacomponent | detects | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Monitor for the termination of processes or services associated with ICS automation protocols and application software which could help detect blocked communications. | relationship--2d65925e-f437-4557-bd8b-4c0d14ffd0b0 | 11 May 2022 | 26 September 2022
| Process Termination | x-mitre-data-component--61f1d40e-f3d0-4cc6-aa2d-937b6204194f | datacomponent | detects | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Monitor for the termination of processes or services associated with ICS automation protocols and application software which could help detect blocked communications. | relationship--3439d550-61d5-40b4-a514-341509d3f701 | 11 May 2022 | 26 September 2022
| Process Termination | x-mitre-data-component--61f1d40e-f3d0-4cc6-aa2d-937b6204194f | datacomponent | detects | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Monitor for the termination of processes or services associated with ICS automation protocols and application software which could help detect blocked communications. | relationship--3aa69e19-f55f-4531-a26e-eb67d6ea24ee | 11 May 2022 | 26 September 2022
| Process Termination | x-mitre-data-component--61f1d40e-f3d0-4cc6-aa2d-937b6204194f | datacomponent | detects | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Monitor processes and command-line arguments to see if critical processes are terminated or stop running. For added context on adversary procedures and background see [Service Stop](https://attack.mitre.org/techniques/T1489). | relationship--70113c21-85f2-4232-8755-233f93864277 | 11 May 2022 | 27 September 2022
| Process/Event Alarm | x-mitre-data-component--4c12c1c8-bcef-4daf-8e5b-fca235f71d9e | datacomponent | detects | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Monitor for loss of expected operational process alarms which could indicate alarms are being suppressed. As noted in the technique description, there may be multiple sources of alarms in an ICS environment. Discrepancies between alarms may indicate the adversary is suppressing some but not all the alarms in the environment. This will not directly detect the technique’s execution, but instead may provide additional evidence that the technique has been used and may complement other detections. | relationship--f2e6103d-ca06-45c4-8fe9-049687fc4361 | 11 May 2022 | 26 September 2022
| Process/Event Alarm | x-mitre-data-component--4c12c1c8-bcef-4daf-8e5b-fca235f71d9e | datacomponent | detects | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Monitor asset alarms which may help identify a loss of communications. Consider correlating alarms with other data sources that indicate traffic has been blocked, such as network traffic. In cases where alternative methods of communicating with outstations exist alarms may still be visible even if command messages are blocked. | relationship--b48be9f9-de0e-4548-ade3-09d47af52798 | 11 May 2022 | 26 September 2022
| Process/Event Alarm | x-mitre-data-component--4c12c1c8-bcef-4daf-8e5b-fca235f71d9e | datacomponent | detects | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Monitor asset alarms which may help identify a loss of communications. Consider correlating alarms with other data sources that indicate traffic has been blocked, such as network traffic. In cases where alternative methods of communicating with outstations exist alarms may still be visible even if reporting messages are blocked. | relationship--1110814e-81ff-4a23-9988-4b93e6f68a2b | 11 May 2022 | 26 September 2022
| Process/Event Alarm | x-mitre-data-component--4c12c1c8-bcef-4daf-8e5b-fca235f71d9e | datacomponent | detects | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Monitor asset alarms which may help identify a loss of communications. Consider correlating alarms with other data sources that indicate traffic has been blocked, such as network traffic. In cases where alternative methods of communicating with outstations exist alarms may still be visible even if messages over serial COM ports are blocked. | relationship--06fc6ec4-7857-4f59-9bbf-df373152bcfd | 11 May 2022 | 26 September 2022
| Process/Event Alarm | x-mitre-data-component--4c12c1c8-bcef-4daf-8e5b-fca235f71d9e | datacomponent | detects | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Monitor for anomalous or unexpected commands that may result in changes to the process operation (e.g., discrete write, logic and device configuration, mode changes) observable via asset application logs. | relationship--cea2f5a7-4871-4c62-a2d5-5a76aadf2d1a | 26 September 2022 | 26 September 2022
| Scheduled Job Creation | x-mitre-data-component--f42df6f0-6395-4f0c-9376-525a031f00c3 | datacomponent | detects | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Monitor for newly constructed scheduled jobs that may attempt to manipulate features of their artifacts to make them appear legitimate or benign to users and/or security tools. | relationship--edb32a4d-62a3-467c-8dfa-f97f1bcbffc6 | 27 September 2022 | 14 October 2022
| Scheduled Job Modification | x-mitre-data-component--faa34cf6-cf32-4dc9-bd6a-8f7a606ff65b | datacomponent | detects | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Monitor for changes made to scheduled jobs that may attempt to manipulate features of their artifacts to make them appear legitimate or benign to users and/or security tools. | relationship--9cf83701-a347-47b4-a67b-280df95b275d | 11 May 2022 | 14 October 2022
| Script Execution | x-mitre-data-component--9f387817-df83-432a-b56b-a8fb7f71eedd | datacomponent | detects | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Monitor for any suspicious attempts to enable script execution on a system. If scripts are not commonly used on a system, but enabled, scripts running out of cycle from patching or other administrator functions are suspicious. Scripts should be captured from the file system when possible, to determine their actions and intent. | relationship--49d941a6-4da2-4516-92d0-1bc64554b2f2 | 11 May 2022 | 29 March 2024
| Script Execution | x-mitre-data-component--9f387817-df83-432a-b56b-a8fb7f71eedd | datacomponent | detects | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Monitor for any suspicious attempts to enable scripts running on a system. If scripts are not commonly used on a system, but enabled, scripts running out of cycle from patching or other administrator functions are suspicious. Scripts should be captured from the file system when possible to determine their actions and intent. Data may also be acquired through Windows system management tools such as [Windows Management Instrumentation](https://attack.mitre.org/techniques/T1047) and [PowerShell](https://attack.mitre.org/techniques/T1059/001). | relationship--8a07f92e-9384-4967-9cd9-ffa08a0e55bf | 30 March 2023 | 30 March 2023
| Script Execution | x-mitre-data-component--9f387817-df83-432a-b56b-a8fb7f71eedd | datacomponent | detects | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | Monitor for any suspicious attempts to enable script execution on a system. If scripts are not commonly used on a system, but enabled, scripts running out of cycle from patching or other administrator functions are suspicious. Scripts should be captured from the file system when possible to determine their actions and intent. | relationship--7c85bff0-8f70-479e-9365-fef1e3fe2b95 | 27 September 2022 | 29 March 2024
| Script Execution | x-mitre-data-component--9f387817-df83-432a-b56b-a8fb7f71eedd | datacomponent | detects | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Monitor for any attempts to enable scripts running on a system would be considered suspicious. If scripts are not commonly used on a system, but enabled, scripts running out of cycle from patching or other administrator functions are suspicious. Scripts should be captured from the file system when possible to determine their actions and intent. | relationship--d6a8b25c-53d4-4df1-8728-20ed4ba5ddab | 11 May 2022 | 14 October 2022
| Script Execution | x-mitre-data-component--9f387817-df83-432a-b56b-a8fb7f71eedd | datacomponent | detects | T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | Monitor for any suspicious attempts to enable script execution on a system. If scripts are not commonly used on a system, but enabled, scripts running out of cycle from patching or other administrator functions are suspicious. Scripts should be captured from the file system when possible to determine their actions and intent. | relationship--55d1eaf7-c3cb-4ff9-8439-96f562d46259 | 25 March 2024 | 29 March 2024
| Service Creation | x-mitre-data-component--5297a638-1382-4f0c-8472-0d21830bf705 | datacomponent | detects | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Monitor for newly constructed services/daemons through Windows event logs for event IDs 4697 and 7045. | relationship--99c0c90e-8526-41d6-80ca-b037598c6326 | 26 September 2022 | 14 October 2022
| Service Creation | x-mitre-data-component--5297a638-1382-4f0c-8472-0d21830bf705 | datacomponent | detects | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Monitor for newly constructed services/daemons that may attempt to manipulate features of their artifacts to make them appear legitimate or benign to users and/or security tools. | relationship--09fe4b04-b1d2-492c-9b10-59b94807ccf9 | 11 May 2022 | 14 October 2022
| Service Metadata | x-mitre-data-component--74fa567d-bc90-425c-8a41-3c703abb221c | datacomponent | detects | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Alterations to the service binary path or the service startup type changed to disabled may be suspicious. | relationship--9d5b9b9c-058f-4782-80aa-9d501442a03d | 11 May 2022 | 14 October 2022
| Service Modification | x-mitre-data-component--66531bc6-a509-4868-8314-4d599e91d222 | datacomponent | detects | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Monitor for changes made to services that may attempt to manipulate features of their artifacts to make them appear legitimate or benign to users and/or security tools. | relationship--b5979643-fefb-460f-b59c-971efe95f121 | 27 September 2022 | 14 October 2022
| Software | x-mitre-data-component--8ed4e6d0-56d7-4e6b-8fa6-41f41631f30d | datacomponent | detects | T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | Collecting information from the I/O image requires analyzing the application program running on the PLC for specific data block reads. Detecting this requires obtaining and analyzing a PLC’s application program, either directly from the device or from asset management platforms. | relationship--fd0340cc-6105-4abd-89d0-60b0d9c00b55 | 27 September 2022 | 27 September 2022
| Software | x-mitre-data-component--8ed4e6d0-56d7-4e6b-8fa6-41f41631f30d | datacomponent | detects | T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | A manipulated I/O image requires analyzing the application program running on the PLC for specific data block writes. Detecting this requires obtaining and analyzing a PLC’s application program, either directly from the device or from asset management platforms. | relationship--44c6bc32-d2e5-42f5-8c2e-42f305cb589b | 27 September 2022 | 27 September 2022
| Software | x-mitre-data-component--8ed4e6d0-56d7-4e6b-8fa6-41f41631f30d | datacomponent | detects | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | Engineering and asset management software will often maintain a copy of the expected program loaded on a controller and may also record any changes made to controller programs and tasks. Data from these platforms can be used to identify modified controller tasking. | relationship--ceafc04b-b31f-419b-82da-41ce9e1ec6e9 | 23 September 2022 | 27 September 2022
| Software | x-mitre-data-component--8ed4e6d0-56d7-4e6b-8fa6-41f41631f30d | datacomponent | detects | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | Engineering and asset management software will often maintain a copy of the expected program loaded on a controller and may also record any changes made to controller programs. Data from these platforms can be used to identify modified controller programs. | relationship--ab0b5170-577b-491e-8508-b9a34dc393c1 | 27 September 2022 | 27 September 2022
| User Account Authentication | x-mitre-data-component--a953ca55-921a-44f7-9b8d-3d40141aa17e | datacomponent | detects | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Monitor for an authentication attempt by a user that may obtain and abuse credentials of existing accounts as a means of gaining Initial Access, Persistence, Privilege Escalation, or Defense Evasion. | relationship--0278ddbc-67d5-444d-8082-bf9974dee920 | 11 May 2022 | 14 October 2022
| Windows Registry Key Deletion | x-mitre-data-component--1177a4c5-31c8-400c-8544-9071166afa0e | datacomponent | detects | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Monitor Windows registry keys that may be deleted or alter generated artifacts on a host system, including logs or captured files such as quarantined malware. For added context on adversary procedures and background see [Indicator Removal](https://attack.mitre.org/techniques/T1070) and applicable sub-techniques. | relationship--8334b3ab-f17f-460e-b627-ad85fc9c2409 | 11 May 2022 | 27 September 2022
| Windows Registry Key Modification | x-mitre-data-component--da85d358-741a-410d-9433-20d6269a6170 | datacomponent | detects | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Monitor HKLM\Software\Policies\Microsoft\Windows NT\DNSClient for changes to the "EnableMulticast" DWORD value. A value of "0" indicates LLMNR is disabled. | relationship--29b85313-645b-4fb1-b5c2-f580d111760b | 26 September 2022 | 14 October 2022
| Windows Registry Key Modification | x-mitre-data-component--da85d358-741a-410d-9433-20d6269a6170 | datacomponent | detects | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Monitor for changes made to Windows Registry keys or values that may delete or alter generated artifacts on a host system, including logs or captured files such as quarantined malware. For added context on adversary procedures and background see [Indicator Removal](https://attack.mitre.org/techniques/T1070) and applicable sub-techniques. | relationship--6b987f2a-3d07-4791-9c1c-e4f6818521e8 | 11 May 2022 | 27 September 2022
| Windows Registry Key Modification | x-mitre-data-component--da85d358-741a-410d-9433-20d6269a6170 | datacomponent | detects | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Monitor for changes made to Windows registry keys and/or values that may stop or disable services on a system to render those services unavailable to legitimate users. | relationship--a7ca9443-f833-4636-9c30-fcaddd3516c6 | 11 May 2022 | 14 October 2022
| Windows Registry Key Modification | x-mitre-data-component--da85d358-741a-410d-9433-20d6269a6170 | datacomponent | detects | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Various techniques enable spoofing a reporting message. Monitor for LLMNR/NBT-NS poisoning via new services/daemons which may be used to enable this technique. For added context on adversary procedures and background see [LLMNR/NBT-NS Poisoning and SMB Relay](https://attack.mitre.org/techniques/T1557/001). | relationship--7a79ff35-319a-4e7d-b8c7-72f0bb0f8978 | 26 September 2022 | 26 September 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--b3b24837-83ed-46c5-ba80-66a832c7072e | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--a86cee0a-dc49-4c95-b5dc-37405337490b | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | Ensure embedded controls and network devices are protected through access management, as these devices often have unknown default accounts which could be used to gain unauthorized access. | relationship--3ed98d8c-de30-499e-9a62-eae0207519f4 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--6637d8e6-6578-4d15-a993-d63ced4c4464 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--e8af0b34-4a67-4966-a34a-c4d1b346ea15 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | Access Management technologies can be used to enforce authorization policies and decisions, especially when existing field devices do not provide capabilities to support user identification and authentication. (Citation: McCarthy, J et al. July 2018) These technologies typically utilize an in-line network device or gateway system to prevent access to unauthenticated users, while also integrating with an authentication service to first verify user credentials. | relationship--efb80069-e4be-4055-bd34-06d1376b4601 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | Ensure embedded controls and network devices are protected through access management, as these devices often have unknown hardcoded accounts which could be used to gain unauthorized access. | relationship--5714c88f-ca54-46b6-b072-cd1d24714ae0 | 29 September 2022 | 29 September 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--f20d8eed-b517-4297-b32a-9a5e0845de9f | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--d1971b32-3a15-4544-9f36-80c05121deb6 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--b7f23af2-e948-4531-af56-1a1b4d03702f | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--ec105f62-2552-41fa-8b07-619dc1bf9b19 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--5ca1d677-b41f-4f1e-b86b-f5637a418829 | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Access Management technologies can help enforce authentication on critical remote service, examples include, but are not limited to, device management services (e.g., telnet, SSH), data access servers (e.g., HTTP, Historians), and HMI sessions (e.g., RDP, VNC). | relationship--c9065f74-556d-4728-8072-f96642e70316 | 12 April 2021 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | All devices or systems changes, including all administrative functions, should require authentication. Consider using access management technologies to enforce authorization on all management interface access attempts, especially when the device does not inherently provide strong authentication and authorization functions. | relationship--68d30c45-766f-48b6-9405-0c969243332b | 21 September 2020 | 06 May 2022
M0801 | Access Management | course-of-action--3992ce42-43e9-4bea-b8db-a102ec3ec1e3 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Authenticate all access to field controllers before authorizing access to, or modification of, a device's state, logic, or programs. Centralized authentication techniques can help manage the large number of field controller accounts needed across the ICS. | relationship--104b4f25-d0a9-41f6-94b3-fa85ee8b1523 | 21 September 2020 | 06 May 2022
M0936 | Account Use Policies | course-of-action--86b455f2-fb63-4043-93a8-32a3a7703a02 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Configure features related to account use like login attempt lockouts, specific login times, and password strength requirements as examples. Consider these features as they relate to assets which may impact safety and availability. (Citation: Keith Stouffer May 2015) | relationship--276aa6a6-e700-470a-8f72-02537ba7be9d | 21 September 2020 | 06 May 2022
M0936 | Account Use Policies | course-of-action--86b455f2-fb63-4043-93a8-32a3a7703a02 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Configure features related to account use like login attempt lockouts, specific login times, and password strength requirements as examples. Consider these features as they relate to assets which may impact safety and availability. (Citation: Keith Stouffer May 2015) | relationship--ea817c7a-9424-4204-90a5-6f8fb86037be | 21 September 2020 | 06 May 2022
M0915 | Active Directory Configuration | course-of-action--2f0160b7-e982-49d7-9612-f19b810f1722 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Consider configuration and use of a network-wide authentication service such as Active Directory, LDAP, or RADIUS capabilities which can be found in ICS devices. (Citation: Keith Stouffer May 2015) (Citation: Schweitzer Engineering Laboratories August 2015) | relationship--eeeaa0d4-0ca0-468e-ae13-43ab7aba61b4 | 21 September 2020 | 06 May 2022
M0949 | Antivirus/Antimalware | course-of-action--faf2b40e-5981-433f-aa46-17458e0026f7 | mitigation | mitigates | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Deploy anti-virus on all systems that support external email. | relationship--bda03e8d-5e06-4470-b786-11b11c7c97c7 | 21 September 2020 | 06 May 2022
M0949 | Antivirus/Antimalware | course-of-action--faf2b40e-5981-433f-aa46-17458e0026f7 | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Install anti-virus software on all workstation and transient assets that may have external access, such as to web, email, or remote file shares. | relationship--6c15ec9f-2b48-419c-adc1-f989833f6187 | 14 October 2021 | 06 May 2022
M0949 | Antivirus/Antimalware | course-of-action--faf2b40e-5981-433f-aa46-17458e0026f7 | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Ensure anti-virus solution can detect malicious files that allow user execution (e.g., Microsoft Office Macros, program installers). | relationship--d3c94120-e6b5-4bd2-88f0-9c73f76b0104 | 21 September 2020 | 06 May 2022
M0913 | Application Developer Guidance | course-of-action--8a3aadd0-b5f4-433a-800e-4893e4196bb7 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Ensure that applications and devices do not store sensitive data or credentials insecurely (e.g., plaintext credentials in code, published credentials in repositories, or credentials in public cloud storage). (Citation: CISA June 2013) | relationship--b69f31c3-6c12-4b81-8e74-9c58ea635fa4 | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Built-in browser sandboxes and application isolation may be used to contain web-based malware. | relationship--ca5c7ae7-5273-4888-bc50-183d6e200972 | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Application isolation will limit the other processes and system features an exploited target can access. Examples of built in features are software restriction policies, AppLocker for Windows, and SELinux or AppArmor for Linux. | relationship--e767c178-e4b2-490a-b544-bb1b2d6c7de4 | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist. (Citation: Dan Goodin March 2017) | relationship--7ff12adb-bc9a-42e5-9cbf-613b200c36dc | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist. (Citation: Dan Goodin March 2017) | relationship--5f03ee5d-534c-454c-aae3-b41130b00286 | 13 April 2021 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Make it difficult for adversaries to advance their operation through exploitation of undiscovered or unpatched vulnerabilities by using sandboxing. Other types of virtualization and application microsegmentation may also mitigate the impact of some types of exploitation. Risks of additional exploits and weaknesses in these systems may still exist. (Citation: Dan Goodin March 2017) | relationship--8fa6fe89-e704-4be4-a15b-50e188084aa3 | 21 September 2020 | 06 May 2022
M0948 | Application Isolation and Sandboxing | course-of-action--059ba11e-e3dc-49aa-84ca-88197f40d4ea | mitigation | mitigates | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Consider the use of application isolation and sandboxing to restrict specific operating system interactions such as access through user accounts, services, system calls, registry, and network access. This may be even more useful in cases where the source of the executed script is unknown. | relationship--2fffbea8-c031-4de8-a451-447bbbe3e224 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Limit access to network infrastructure and resources that can be used to reshape traffic or otherwise produce AiTM conditions. | relationship--b47dbc50-fd8f-4e5b-bb3d-e93b68bf5497 | 21 September 2020 | 21 March 2023
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Consider periodic reviews of accounts and privileges for critical and sensitive repositories. | relationship--2ff82993-5010-4450-89e7-341f449f3263 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | Perform audits or scans of systems, permissions, insecure software, insecure configurations, etc. to identify potential weaknesses. Perform periodic integrity checks of the device to validate the correctness of the firmware, software, programs, and configurations. Integrity checks, which typically include cryptographic hashes or digital signatures, should be compared to those obtained at known valid states, especially after events like device reboots, program downloads, or program restarts. | relationship--b72b7dfd-f134-4324-84b8-52ff13fc6b5c | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | Provide the ability to verify the integrity of controller tasking. While techniques like CRCs and checksums are commonly used, they are not cryptographically secure and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used. (Citation: IEC February 2019) | relationship--698d7c50-daab-4087-a7b4-b2bc8dfd81a7 | 13 April 2021 | 25 September 2023
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | Provide the ability to verify the integrity and authenticity of changes to parameter values. | relationship--5bf8473c-3c60-4a8a-8514-c2b50ab8a92d | 21 September 2020 | 25 September 2023
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | Provide the ability to verify the integrity of control logic or programs loaded on a controller. While techniques like CRCs and checksums are commonly used, they are not cryptographically strong and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used. (Citation: IEC February 2019) | relationship--34ac1b1b-1103-4fc9-a62e-f1dd1451b28b | 13 April 2021 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Perform integrity checks of firmware before uploading it on a device. Utilize cryptographic hashes to verify the firmware has not been tampered with by comparing it to a trusted hash of the firmware. This could be from trusted data sources (e.g., vendor site) or through a third-party verification service. | relationship--65a45501-10de-46a2-89bf-03bbf17aba33 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Provide the ability to verify the integrity of programs downloaded on a controller. While techniques like CRCs and checksums are commonly used, they are not cryptographically secure and can be vulnerable to collisions. Preferably cryptographic hash functions (e.g., SHA-2, SHA-3) should be used. (Citation: IEC February 2019) | relationship--1c3d966a-5995-48ed-919d-25b972010fe9 | 21 September 2020 | 25 September 2023
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | Review the integrity of project files to verify they have not been modified by adversary behavior. Verify a cryptographic hash for the file with a known trusted version, or look for other indicators of modification (e.g., timestamps). | relationship--f9aa3364-a1eb-4776-ae03-c39b250545a0 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | Audit the integrity of PLC system and application code functionality, such as the manipulation of standard function blocks (e.g., Organizational Blocks) that manage the execution of application logic programs. (Citation: IEC February 2019) | relationship--5de6bf53-0a02-439b-a8d0-248fa9640a36 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | Perform audits or scans of systems, permissions, insecure software, insecure configurations, etc. to identify potential weaknesses. Perform periodic integrity checks of the device to validate the correctness of the firmware, software, programs, and configurations. Integrity checks, which typically include cryptographic hashes or digital signatures, should be compared to those obtained at known valid states, especially after events like device reboots, program downloads, or program restarts. | relationship--0491ef92-2941-4841-9fe6-2e1809788b52 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Perform integrity checks of firmware before uploading it on a device. Utilize cryptographic hashes to verify the firmware has not been tampered with by comparing it to a trusted hash of the firmware. This could be from trusted data sources (e.g., vendor site) or through a third-party verification service. | relationship--04fa6b94-d633-40ff-9ab2-88f58c07c3e1 | 21 September 2020 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Integrity checking of transient assets can include performing the validation of the booted operating system and programs using TPM-based technologies, such as Secure Boot and Trusted Boot. (Citation: Emerson Exchange) It can also include verifying filesystem changes, such as programs and configuration files stored on the system, executing processes, libraries, accounts, and open ports. (Citation: National Security Agency February 2016) | relationship--5041e17d-6349-4589-8c61-7b43964b5f9b | 14 October 2021 | 06 May 2022
M0947 | Audit | course-of-action--bcf91ebc-f316-4e19-b2f6-444e9940c697 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Routinely audit source code, application configuration files, open repositories, and public cloud storage for insecure use and storage of credentials. | relationship--baf7daf3-2116-4051-91b5-f82e146167d0 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Restrict configurations changes and firmware updating abilities to only authorized individuals. | relationship--ff3f0668-98df-44c1-88c2-711f05720eb8 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | All field controllers should restrict operating mode changes to only required authenticated users (e.g., engineers, field technicians), preferably through implementing a role-based access mechanism. Further, physical mechanisms (e.g., keys) can also be used to limit unauthorized operating mode changes. | relationship--eeeff03f-7436-4f76-8591-42075e6647d4 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--b8f6d6a8-e668-4596-8ec2-41c5d1bd211d | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--6b5fd6d8-ef70-4896-b1a4-7b6c29c3a0d4 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | All APIs used to perform execution, especially those hosted on embedded controllers (e.g., PLCs), should provide adequate authorization enforcement of user access. Minimize user's access to only required API calls. (Citation: MITRE June 2020) | relationship--754521fc-4306-4daa-831b-6b6fb45847e2 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Only authorized personnel should be able to change settings for alarms. | relationship--6b5d2643-b399-43aa-8ab1-7557a0446b07 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | All field controllers should restrict the modification of controller tasks to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--4653847b-c089-4435-9159-6f76353833f7 | 25 September 2023 | 25 September 2023
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | All field controllers should restrict the modification of parameter values to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. They should also restrict online edits and enable write protection for parameters. | relationship--e6be2fb4-3815-4e52-8dec-2aed1dc3b7cf | 21 September 2020 | 25 September 2023
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | All field controllers should restrict the modification of programs to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--d2a434c7-4428-435e-ae6b-e54012f29606 | 25 September 2023 | 25 September 2023
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Systems and devices should restrict access to any data with potential confidentiality concerns, including point and tag information. | relationship--243ad7b2-546c-4bf2-a3c0-1438b13e197d | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | All field controllers should restrict the download of programs, including online edits and program appends, to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--a7caa7f2-cfb9-4fc9-ae8d-49349b6c260f | 21 September 2020 | 25 September 2023
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | All field controllers should restrict program uploads to only certain users (e.g., engineers, field technician), preferably through implementing a role-based access mechanism. | relationship--5ae1cf3a-2603-4bf9-ace3-5b1ee5d8d757 | 21 September 2020 | 06 May 2022
M0800 | Authorization Enforcement | course-of-action--e0d38502-decb-481d-ad8b-b8f0a0c330bd | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Provide privileges corresponding to the restriction of a GUI session to control system operations (examples include HMI read-only vs. read-write modes). Ensure local users, such as operators and engineers, are giving prioritization over remote sessions and have the authority to regain control over a remote session if needed. Prevent remote access sessions (e.g., RDP, VNC) from taking over local sessions, especially those used for ICS control, especially HMIs. | relationship--4966e63c-ca05-466d-91f9-41d799a54471 | 12 April 2021 | 06 May 2022
M0946 | Boot Integrity | course-of-action--8ac1d6e1-b07f-476a-9732-84984ebc2405 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Check the integrity of the existing BIOS or EFI to determine if it is vulnerable to modification. Use Trusted Platform Module technology. (Citation: N/A) Move system's root of trust to hardware to prevent tampering with the SPI flash memory. (Citation: ESET Research Whitepapers September 2018) Technologies such as Intel Boot Guard can assist with this. (Citation: Intel) | relationship--0c284ce0-0be2-4164-b686-7c383b246aec | 21 September 2020 | 21 March 2023
M0946 | Boot Integrity | course-of-action--8ac1d6e1-b07f-476a-9732-84984ebc2405 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Check the integrity of the existing BIOS or EFI to determine if it is vulnerable to modification. Use Trusted Platform Module technology. (Citation: N/A) Move system's root of trust to hardware to prevent tampering with the SPI flash memory. (Citation: ESET Research Whitepapers September 2018) Technologies such as Intel Boot Guard can assist with this. (Citation: Intel) | relationship--a47cd7b9-2b73-480c-a8ab-2dfa908e02ea | 21 September 2020 | 21 March 2023
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Require signed binaries. | relationship--b9e82422-b072-494f-99c1-fcab07b90133 | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | Utilize code signatures to verify the integrity and authenticity of programs installed on safety or control assets, including the associated controller tasking. | relationship--973f5884-a076-413e-ac96-f0bd01375fb6 | 13 April 2021 | 25 September 2023
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | Utilize code signatures to verify the integrity and authenticity of programs installed on safety or control assets. | relationship--a91002fe-21b2-4417-9c23-af712a7a035c | 13 April 2021 | 25 September 2023
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Devices should verify that firmware has been properly signed by the vendor before allowing installation. | relationship--46332a77-2fd6-4033-96cf-6163172775ec | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Utilize code signatures to verify the integrity and authenticity of programs downloaded to the device. | relationship--cb30d507-edc6-4197-947c-7b3a6e395c0d | 21 September 2020 | 25 September 2023
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | Allow for code signing of any project files stored at rest to prevent unauthorized tampering. Ensure the signing keys are not easily accessible on the same system. | relationship--f9c29dd4-1c5e-4f7e-b60a-862319a6d0a0 | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | Digital signatures may be used to ensure application DLLs are authentic prior to execution. | relationship--2971151c-0e8a-4567-84dc-01cf5dd35005 | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | When available utilize hardware and software root-of-trust to verify the authenticity of a system. This may be achieved through cryptographic means, such as digital signatures or hashes, of critical software and firmware throughout the supply chain. | relationship--d6a2a1a8-8f5b-4e94-8fce-8edd8a17627a | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Devices should verify that firmware has been properly signed by the vendor before allowing installation. | relationship--3be9d4d1-17e1-4f3e-b22a-edad8cf0c343 | 21 September 2020 | 06 May 2022
M0945 | Code Signing | course-of-action--71eb7dad-07eb-4bbc-9df0-ac57bf2fba4a | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Prevent the use of unsigned executables, such as installers and scripts. | relationship--e09e253c-fd28-49ae-988e-1f80d769e8b8 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--afd63145-6033-49e4-ad43-d0b35fa5ed88 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Communication authenticity will ensure that any messages tampered with through AiTM can be detected, but cannot prevent eavesdropping on these. In addition, providing communication authenticity around various discovery protocols, such as DNS, can be used to prevent various AiTM procedures. | relationship--f6ff74c2-d088-4252-a8e0-189574863765 | 21 September 2020 | 21 March 2023
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--12a6c5bc-c685-4249-b8c6-e6d49aa2b9ed | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--808c57e7-72ef-4860-b9ea-8ea072e2385a | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--491455dc-f7c8-4e12-811b-b8c5c041b4c3 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--b628d878-4f35-4580-8d42-26984d13821e | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--41adaf0b-b7ae-4bdb-9a5b-567fd0911d7a | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--7aa93b40-80da-4bb6-8a7c-88e5f5e44669 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--dbdd9a97-81df-40b8-b72d-ac67d121b8b3 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--ebc34374-2dee-4dc1-b0b7-f31ae94dab11 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--0df0cb6d-0067-48b2-a33e-495415713ab7 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--7db9687b-7099-4cb6-a040-bc32fc549a81 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--147c2158-b2af-4d88-9d59-594c67a9200e | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Protocols used for device management should authenticate all network messages to prevent unauthorized system changes. | relationship--234da455-b795-4788-bc5d-22b4b58b2dc7 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Protocols used for control functions should provide authenticity through MAC functions or digital signatures. If not, utilize bump-in-the-wire devices or VPNs to enforce communication authenticity between devices that are not capable of supporting this (e.g., legacy controllers, RTUs). | relationship--6e3c2c04-0838-4863-80a7-d73ef5ac6a64 | 21 September 2020 | 06 May 2022
M0802 | Communication Authenticity | course-of-action--c7257b6e-4159-4771-b1f3-2bb93adaecac | mitigation | mitigates | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Do not inherently rely on the authenticity provided by the network/link layer (e.g., 802.11, LTE, 802.15.4), as link layer equipment may have long lifespans and protocol vulnerabilities may not be easily patched. Provide defense-in-depth by implementing authenticity within the associated application-layer protocol, or through a network-layer VPN. (Citation: CISA March 2010) Furthermore, ensure communication schemes provide strong replay protection, employing techniques such as timestamps or cryptographic nonces. | relationship--3ab912a4-70aa-45f8-b2ef-57113dde2cfa | 21 September 2020 | 06 May 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--a717ccc7-0fe6-4a83-951f-5a89037ed927 | 30 March 2023 | 30 March 2023
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Utilize central storage servers for critical operations where possible (e.g., historians) and keep remote backups. For outstations, use local redundant storage for event recorders. Have backup control system platforms, preferably as hot-standbys to respond immediately to data destruction events. (Citation: National Institute of Standards and Technology April 2013) | relationship--6be4cef2-3d54-4cd8-97df-8a8b37c03605 | 21 September 2020 | 06 May 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--44c857cf-7a4e-405a-87ca-7f6d79000589 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--c2fe42b4-6750-4b51-86b7-6c37fbfdef2d | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--b8d6e550-18fe-49ad-9964-7802bbe0cb58 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--6ad39b3a-a962-457f-852c-be7fc615e22f | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--dda89758-9d0b-446d-b594-85acc7f9cb90 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--eecca3e7-4db5-40d4-b04c-13f84701acb3 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--578117b2-0f4b-4d75-a2dc-3ee45976e616 | 21 September 2020 | 19 October 2022
M0953 | Data Backup | course-of-action--ad12819e-3211-4291-b360-069f280cff0a | mitigation | mitigates | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | Take and store data backups from end user systems and critical servers. Ensure backup and storage systems are hardened and kept separate from the corporate network to prevent compromise. Maintain and exercise incident response plans (Citation: Department of Homeland Security October 2009), including the management of gold-copy back-up images and configurations for key systems to enable quick recovery and response from adversarial activities that impact control, view, or availability. | relationship--c64f2ed2-f7a7-4333-b0d3-d687ffb7ad6b | 21 September 2020 | 19 October 2022
M0803 | Data Loss Prevention | course-of-action--337c4e2a-21a7-4d9a-bfee-9efd6cebf0e5 | mitigation | mitigates | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Data loss prevention can restrict access to sensitive data and detect sensitive data that is unencrypted. | relationship--8f7ccb2b-de2a-4a5c-9f1e-d5e58e69efa8 | 30 March 2023 | 30 March 2023
M0803 | Data Loss Prevention | course-of-action--337c4e2a-21a7-4d9a-bfee-9efd6cebf0e5 | mitigation | mitigates | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | Apply DLP to protect the confidentiality of information related to operational processes, facility locations, device configurations, programs, or databases that may have information that can be used to infer organizational trade-secrets, recipes, and other intellectual property (IP). | relationship--bc74ff8f-d5fa-40fb-8c0b-f16af3ff36e3 | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Disable unnecessary legacy network protocols that may be used for AiTM if applicable. | relationship--d16e8909-d055-4174-aeb1-22c0613b2f73 | 21 September 2020 | 21 March 2023
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | Consider removing or restricting features that are unnecessary to an asset's intended function within the control environment. | relationship--7c2edd6c-5189-4ba9-af3d-bdaff4a699ca | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | Ensure that unnecessary ports and services are closed to prevent risk of discovery and potential exploitation. | relationship--ca64a927-f050-41b3-80d3-93d22cdef26a | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Ensure remote commands that enable device shutdown are disabled if they are not necessary. Examples include DNP3's 0x0D function code or unnecessary device management functions. | relationship--8ca2fe75-9bb3-4af5-8fee-accd33d6d2ec | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Ensure that unnecessary ports and services are closed to prevent risk of discovery and potential exploitation. | relationship--4369da69-bb09-4cc8-8600-081a450f50e0 | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Consider removal of remote services which are not regularly in use, or only enabling them when required (e.g., vendor remote access). Ensure all external remote access point (e.g., jump boxes, VPN concentrator) are configured with least functionality, especially the removal of unnecessary services. (Citation: Department of Homeland Security September 2016) | relationship--a847aa03-ea56-47d1-8f4e-f9e0dd9707a0 | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Consider the disabling of features such as AutoRun. | relationship--d8f45959-e0fc-4b4f-a074-a3acea926300 | 21 September 2020 | 06 May 2022
M0942 | Disable or Remove Feature or Program | course-of-action--d0909119-2f71-4923-87db-b649881672d7 | mitigation | mitigates | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Consider removal or disabling of programs and features which may be used to run malicious scripts (e.g., scripting language IDEs, PowerShell, visual studio). | relationship--590bdd67-31ef-4edd-b2ac-2bd1b98da19c | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware. | relationship--41b87fd8-6e4d-4e53-a282-c85292fdaa22 | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Ensure that wired and/or wireless traffic is encrypted when feasible. Use best practices for authentication protocols, such as Kerberos, and ensure web traffic that may contain credentials is protected by SSL/TLS. (Citation: Keith Stouffer May 2015) | relationship--c5fd0969-c151-4849-94c2-83e2e208cff7 | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware. | relationship--43bdf580-b98f-49cf-92d5-3dac50450c86 | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Utilize strong cryptographic techniques and protocols to prevent eavesdropping on network communications. | relationship--b363cbbb-679c-47e0-8ad0-af98ebf51e60 | 21 September 2020 | 06 May 2022
M0808 | Encrypt Network Traffic | course-of-action--7f153c28-e5f1-4764-88fb-eea1d9b0ad4a | mitigation | mitigates | T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | Utilize strong cryptographic techniques and protocols to prevent eavesdropping on network communications. (Citation: Bastille April 2017) | relationship--3478c49c-594b-4224-b7f9-2b0b09c67288 | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Information which is sensitive to the operation and architecture of the process environment may be encrypted to ensure confidentiality and restrict access to only those who need to know. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--50a2b289-7bce-405d-8515-c2b5424cce5c | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Information which is sensitive to the operation and architecture of the process environment may be encrypted to ensure confidentiality and restrict access to only those who need to know. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--03e80e3c-28b9-4e7f-8b17-7c86d1483b91 | 30 March 2023 | 30 March 2023
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware. | relationship--09977105-562f-4f45-a151-27a11a18031e | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | When at rest, project files should be encrypted to prevent unauthorized changes. (Citation: National Institute of Standards and Technology April 2013) | relationship--c78f497f-01c3-4efb-aa74-92b700b9c02b | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | The encryption of firmware should be considered to prevent adversaries from identifying possible vulnerabilities within the firmware. | relationship--cf8ac499-8c1c-4615-b933-7587f1b9488b | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | Encrypt any operational data with strong confidentiality requirements, including organizational trade-secrets, recipes, and other intellectual property (IP). | relationship--cb4d802e-df5b-4017-81dd-47f65fff23a3 | 21 September 2020 | 06 May 2022
M0941 | Encrypt Sensitive Information | course-of-action--9f99fcfd-772e-4e63-9d39-e45612e546dc | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Consider implementing full disk encryption, especially if engineering workstations are transient assets that are more likely to be lost, stolen, or tampered with. (Citation: National Institute of Standards and Technology April 2013) | relationship--2fbb7867-79c5-4d45-9876-98c4041dd72e | 14 October 2021 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | Execution prevention may block malicious software from accessing protected resources through the command line interface. | relationship--75366cbf-e45f-4cfd-9e76-5af4dfe10766 | 21 September 2020 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | Minimize the exposure of API calls that allow the execution of code. | relationship--3d676c1b-2650-4599-8a57-790c55f9977d | 21 September 2020 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Use tools that restrict program execution via application control by attributes other than file name for common system and application utilities. | relationship--cca191a1-3c50-4d4f-8f79-4247e58af610 | 21 September 2020 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | Minimize the exposure of API calls that allow the execution of code. | relationship--446c95ea-5178-4ae9-8f92-cb20dd50f7de | 13 April 2021 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | Execution prevention may prevent malicious scripts from accessing protected resources. | relationship--2f64b5aa-7e4d-4a5e-9960-69a63ad25083 | 21 September 2020 | 06 May 2022
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | Disallow the execution of applications/programs which are not required for normal system functions, including any specific command-line arguments which may allow the execution of proxy commands or application binaries. | relationship--337f366d-3d76-470c-8ee2-0e2252648282 | 25 March 2024 | 25 March 2024
M0938 | Execution Prevention | course-of-action--4fa717d9-cabe-47c8-8cdd-86e9e2e37f30 | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Application control may be able to prevent the running of executables masquerading as other files. | relationship--07f4d65d-4572-450f-8cb2-908fee97bd67 | 21 September 2020 | 06 May 2022
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Utilize exploit protection to prevent activities which may be exploited through malicious web sites. | relationship--e5afc447-a241-4773-9a8a-3d6fd205d926 | 21 September 2020 | 06 May 2022
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Web Application Firewalls may be used to limit exposure of applications to prevent exploit traffic from reaching the application. (Citation: Karen Scarfone; Paul Hoffman September 2009) | relationship--ad7fd147-066e-4ed5-aa9d-7b2f1771150d | 21 September 2020 | 06 May 2022
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. (Citation: Microsoft Security Response Center August 2017) Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. (Citation: Wikipedia) Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted. | relationship--238f967a-0c29-4aa3-bbb5-3dc593473bbf | 21 September 2020 | 21 March 2023
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. (Citation: Microsoft Security Response Center August 2017) Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. (Citation: Wikipedia) Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted. | relationship--3b6567a9-6213-4db4-a069-1a86b1098b63 | 13 April 2021 | 21 March 2023
M0950 | Exploit Protection | course-of-action--49363b74-d506-4342-bd63-320586ebadb9 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Security applications that look for behavior used during exploitation such as Windows Defender Exploit Guard (WDEG) and the Enhanced Mitigation Experience Toolkit (EMET) can be used to mitigate some exploitation behavior. (Citation: Microsoft Security Response Center August 2017) Control flow integrity checking is another way to potentially identify and stop a software exploit from occurring. (Citation: Wikipedia) Many of these protections depend on the architecture and target application binary for compatibility and may not work for all software or services targeted. | relationship--47f15a06-8675-4698-833d-bd141ed9e755 | 21 September 2020 | 21 March 2023
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Filter for protocols and payloads associated with firmware activation or updating activity. | relationship--ee89466e-0655-4217-844d-fb8ea4f76247 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Allow/denylists can be used to block access when excessive I/O connections are detected from a system or device during a specified time period. | relationship--9a44b2a8-9f4c-43df-9174-1cba6e165886 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | Traffic to known anonymity networks and C2 infrastructure can be blocked through the use of network allow and block lists. It should be noted that this kind of blocking may be circumvented by other techniques likeDomain Fronting. | relationship--7bfaf0ff-6d88-460f-aa32-3fb0267b4f20 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages. | relationship--64db6a39-64d2-4999-97d7-91c28c32f42e | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Application denylists can be used to block automation protocol functions used to initiate device shutdowns or restarts, such as DNP3's 0x0D function code, or vulnerabilities that can be used to trigger device shutdowns (e.g., CVE-2014-9195, CVE-2015-5374). | relationship--ca768c2a-0f14-471c-90a5-bce649e88d51 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Filter for protocols and payloads associated with firmware activation or updating activity. | relationship--3da977ab-c863-4e6f-a5b7-68173160da00 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages. | relationship--686cbd74-ef49-4e77-9599-21777d3a4738 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Filter for protocols and payloads associated with program download activity to prevent unauthorized device configurations. | relationship--366a4cd1-aa95-4985-9d80-b45a2551e298 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Filter for protocols and payloads associated with program upload activity to prevent unauthorized access to device configurations. | relationship--baf4bd30-4213-43c3-b70c-54418e734caf | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Filter application-layer protocol messages for remote services to block any unauthorized activity. | relationship--f0c8a954-c1a0-453a-9c1d-484305abdab2 | 12 April 2021 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid reporting messages. | relationship--575f0e0b-d68d-432b-abb3-cbd3e641fc88 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid reporting messages. | relationship--d08fdedd-12f6-4681-9167-70d070432dee | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Filter for protocols and payloads associated with firmware activation or updating activity. | relationship--dc46ffc2-eac7-4491-8d2a-46cf8e2e963f | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Perform inline allowlisting of automation protocol commands to prevent devices from sending unauthorized command or reporting messages. Allow/denylist techniques need to be designed with sufficient accuracy to prevent the unintended blocking of valid messages. | relationship--48489baf-56c2-423e-964a-0a61688e4a19 | 21 September 2020 | 06 May 2022
M0937 | Filter Network Traffic | course-of-action--11f242bc-3121-438c-84b2-5cbd46a4bb17 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Consider using IP allowlisting along with user account management to ensure that data access is restricted not only to valid users but only from expected IP ranges to mitigate the use of stolen credentials to access data. | relationship--5dfa5bad-8b0b-4884-bf01-04ea89e3ccf7 | 21 September 2020 | 06 May 2022
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918) | relationship--63453d2f-30f6-40ab-b32c-506d940ecd20 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--22448288-32d9-4d2c-be16-0784e119fff1 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--0a5d2136-e1f5-4a54-be64-a558f918bf0d | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--49d38b21-5ce5-48d9-a356-639fc6c7a53d | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--3a6cd53d-0d4e-4cf8-8edf-f9ebde4faac4 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | All APIs on remote systems or local processes should require the authentication of users before executing any code or system changes. | relationship--dded2d68-35c7-42c4-af10-efe7731673e3 | 21 September 2020 | 06 May 2022
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--03a9cdc7-3cc5-43e3-9a9c-97d1c4310e35 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management. | relationship--5f5c38f6-aa3e-4447-a2d3-a76830ab36b0 | 25 September 2023 | 25 September 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | All field controllers should require that user authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management. | relationship--af20f409-05ed-42c3-ae3e-09b047b84875 | 25 September 2023 | 25 September 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support Account Use Policies, Password Policies, and User Account Management. | relationship--fad25140-73de-40d5-a010-3464188db973 | 25 September 2023 | 25 September 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--7d6c4a00-acde-40af-bf91-a4ef009cf135 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--79324bdd-cdab-4d0a-af60-af1047c1d117 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--fa1bde35-63d9-4c5c-969b-2c17c29089fa | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | All field controllers should require users to authenticate for all remote or local management sessions. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--f45c2df8-30e7-45d0-8067-7b2870767574 | 21 September 2020 | 08 March 2023
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | All remote services should require strong authentication before providing user access. | relationship--6d1906b4-e815-4688-86f1-ce61d403f8c6 | 21 September 2020 | 06 May 2022
M0804 | Human User Authentication | course-of-action--66cfe23e-34b6-4583-b178-ed6a412db2b0 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Devices that allow remote management of firmware should require authentication before allowing any changes. The authentication mechanisms should also support [Account Use Policies](https://attack.mitre.org/mitigations/M0936), [Password Policies](https://attack.mitre.org/mitigations/M0927), and [User Account Management](https://attack.mitre.org/mitigations/M0918). | relationship--17fdec71-98e8-4314-a1be-037edede58bd | 21 September 2020 | 08 March 2023
M0935 | Limit Access to Resource Over Network | course-of-action--49b306c1-a046-42c5-a4d2-30f264ada110 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Limit access to remote services through centrally managed concentrators such as VPNs and other managed remote access systems. | relationship--2daeeaaa-5b4b-4bb7-a94d-78a5749027ca | 21 September 2020 | 06 May 2022
M0934 | Limit Hardware Installation | course-of-action--9e3adcad-0b8f-4ecc-a2f3-06f607f53bf0 | mitigation | mitigates | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Enforce system policies or physical restrictions to limit hardware such as USB devices on critical assets. | relationship--8f90363e-2825-4178-807f-9268a28760fa | 21 September 2020 | 06 May 2022
M0805 | Mechanical Protection Layers | course-of-action--8bc4a54e-810c-4600-8b6c-08fa8413a401 | mitigation | mitigates | T0879 | Damage to Property | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | technique | Protection devices should have minimal digital components to prevent exposure to related adversarial techniques. Examples include interlocks, rupture disks, release valves, etc. (Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004) | relationship--e607bb66-e53f-4684-b3f1-36a997e27d01 | 21 September 2020 | 06 May 2022
M0805 | Mechanical Protection Layers | course-of-action--8bc4a54e-810c-4600-8b6c-08fa8413a401 | mitigation | mitigates | T0880 | Loss of Safety | attack-pattern--5fa00fdd-4a55-4191-94a0-564181d7fec2 | technique | Protection devices should have minimal digital components to prevent exposure to related adversarial techniques. Examples include interlocks, rupture disks, release valves, etc. (Citation: A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004) | relationship--242b5a0d-e4e8-4ceb-a975-cf8efd64e981 | 21 September 2020 | 06 May 2022
M0806 | Minimize Wireless Signal Propagation | course-of-action--fce6866f-9a87-4d3e-a73c-f02d8937fe0e | mitigation | mitigates | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Techniques can include (i) reducing transmission power on wireless signals, (ii) adjusting antenna gain to prevent extensions beyond organizational boundaries, and (iii) employing RF shielding techniques to block excessive signal propagation. (Citation: DHS National Urban Security Technology Laboratory April 2019) | relationship--b2e10e48-8bd9-472a-9c6f-1d38650e8df1 | 21 September 2020 | 06 May 2022
M0806 | Minimize Wireless Signal Propagation | course-of-action--fce6866f-9a87-4d3e-a73c-f02d8937fe0e | mitigation | mitigates | T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | Reduce the range of RF communications to their intended operating range when possible. Propagation reduction methods may include (i) reducing transmission power on wireless signals, (ii) adjusting antenna gain to prevent extensions beyond organizational boundaries, and (iii) employing RF shielding techniques to block excessive signal propagation. (Citation: DHS National Urban Security Technology Laboratory April 2019) | relationship--2f6b635b-1441-4ef0-9289-1ed6b9098d4a | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | Once an adversary has access to a remote GUI they can abuse system features, such as required HMI functions. | relationship--2b62e4c0-9267-47bd-8f4d-0394b13fb566 | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | This technique may not be effectively mitigated against, consider controls for assets and processes that lead to the use of this technique. | relationship--17ae41a5-cb45-4935-bec1-ea0c8bfb2f34 | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | This technique may not be effectively mitigated against, consider controls for assets and processes that lead to the use of this technique. | relationship--b5bb5ec3-aa3c-4734-8425-4be80c5658a9 | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | This type of attack technique cannot be easily mitigated with preventive controls since it is based on the abuse of system features. | relationship--5804ae3d-0daf-47a5-b026-d42878f55803 | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | Network connection enumeration is likely obtained by using common system tools (e.g., netstat, ipconfig). | relationship--ae7487f1-a2d0-443d-b418-cd726c5ac15f | 21 September 2020 | 06 May 2022
M0816 | Mitigation Limited or Not Effective | course-of-action--469b78dd-a54d-4f7c-8c3b-4a1dd916b433 | mitigation | mitigates | T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | Preventing screen capture on a device may require disabling various system calls supported by the operating systems (e.g., Microsoft WindowsGraphicsCaputer APIs), however, these may be needed for other critical applications. | relationship--b5e52859-8dab-4e7e-af70-bb38c6993c98 | 21 September 2020 | 06 May 2022
M0932 | Multi-factor Authentication | course-of-action--ddf3e568-f065-49e2-9106-42029a28ddbd | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Use strong multi-factor authentication for remote service accounts to mitigate an adversary's ability to leverage stolen credentials. Be aware of multi-factor authentication interception techniques for some implementations. | relationship--dc35c44a-a90c-48a1-8811-af2618216e42 | 21 September 2020 | 17 March 2023
M0932 | Multi-factor Authentication | course-of-action--ddf3e568-f065-49e2-9106-42029a28ddbd | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Use multi-factor authentication wherever possible. | relationship--58a0fd57-ea5f-46b0-84ac-c5b963fb7e94 | 21 September 2020 | 06 May 2022
M0932 | Multi-factor Authentication | course-of-action--ddf3e568-f065-49e2-9106-42029a28ddbd | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Integrating multi-factor authentication (MFA) as part of organizational policy can greatly reduce the risk of an adversary gaining access to valid credentials that may be used for additional tactics such as initial access, lateral movement, and collecting information. MFA can also be used to restrict access to cloud resources and APIs. | relationship--9b412b1f-2dd0-4e7f-8364-f625181ba1db | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--10626671-941d-4a82-a835-56059058ef87 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--ade12d27-13bb-4ebf-be08-7039cf699682 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--6f0384e6-73c8-4fc7-bc0c-0a8c2bfa473d | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--c6562519-81c5-4eca-a815-f46ac0ed4bcc | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--7fc9fbfc-ab9f-4189-bc1f-d473e9ef36b5 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Implement network allowlists to minimize serial comm port access to only authorized hosts, such as comm servers and RTUs. | relationship--cd297a7b-4b02-407e-a798-e36fef4cf3a1 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Utilize network allowlists to restrict unnecessary connections to network devices (e.g., comm servers, serial to ethernet converters) and services, especially in cases when devices have limits on the number of simultaneous sessions they support. | relationship--461e81a2-c7ad-499e-908d-05ef2f7bd9cd | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--ab60fe4a-5860-410a-8bca-2cdbea95e5f8 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device. Allowlist techniques that operate at the application layer (e.g., DNP3, Modbus, HTTP) are addressed in the [Filter Network Traffic](https://attack.mitre.org/mitigations/M0937) mitigation. | relationship--c8dd2735-bd04-4413-847d-316b77c6de19 | 21 September 2020 | 08 March 2023
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0879 | Damage to Property | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--58269882-7e8d-4d24-b7a3-dbef6196cb61 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--a22fabd2-836e-4141-9219-c76cc10138ec | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--00e6c22b-9275-4039-b6d4-2ac0680325d6 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--2cd79563-0f5a-44a1-9be4-6dc330855d64 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--f0ac1d07-fccd-4330-93cf-fbc985ee6fb9 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--2ecc567f-3aaa-4bd8-935f-4808d177a552 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--4256a0c2-437d-4a4c-88ac-d08d3041b8c1 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--c0efb24a-2329-401a-bba6-817f2867bb3f | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device. | relationship--842a2b85-4e77-4eb6-99e1-c4a231aadf48 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--652a68a2-a26b-4e8c-86dd-fd83187ed043 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--ce7c17b7-b60d-4ebd-9014-2c421a64d70a | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | Network allowlists can be implemented through either host-based files or system host files to specify what external connections (e.g., IP address, MAC address, port, protocol) can be made from a device. Allowlist techniques that operate at the application layer (e.g., DNP3, Modbus, HTTP) are addressed in the [Filter Network Traffic](https://attack.mitre.org/mitigations/M0937) mitigation. | relationship--d854cc38-adf7-485d-96b5-70606f6cb87e | 21 September 2020 | 08 March 2023
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--3dde2b07-7c30-4a18-a9df-f85db84f9b14 | 21 September 2020 | 06 May 2022
M0807 | Network Allowlists | course-of-action--aadac250-bcdc-44e3-a4ae-f52bd0a7a16a | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Use host-based allowlists to prevent devices from accepting connections from unauthorized systems. For example, allowlists can be used to ensure devices can only connect with master stations or known management/engineering workstations. (Citation: Department of Homeland Security September 2016) | relationship--b960c5ed-1ea8-4dde-9203-c02d291d3bc6 | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Network intrusion detection and prevention systems that can identify traffic patterns indicative of AiTM activity can be used to mitigate activity at the network level. | relationship--b13417ea-d8da-497f-818f-d2d90562039a | 21 September 2020 | 21 March 2023
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific protocol used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools. (Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014) | relationship--7dedeb73-ef90-4282-a635-cc37326773af | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific C2 protocol used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools. (Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014) | relationship--7411b05d-209a-4907-83ce-00ab1538fbac | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware or unusual data transfer over known tools and protocols like FTP can be used to mitigate activity at the network level. Signatures are often for unique indicators within protocols and may be based on the specific obfuscation technique used by a particular adversary or tool and will likely be different across various malware families and versions. Adversaries will likely change tool C2 signatures over time or construct protocols in such a way as to avoid detection by common defensive tools. (Citation: Gardiner, J., Cova, M., Nagaraja, S February 2014) | relationship--c69eab3c-861c-45f5-8858-a595fcc7e6f6 | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Network intrusion prevention systems and systems designed to scan and remove malicious email attachments can be used to block activity. | relationship--9a607f89-85b8-4fba-8eb7-7e4900ea693f | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | Network intrusion detection and prevention systems that use network signatures to identify traffic for specific adversary malware can be used to mitigate activity at the network level. | relationship--5be1f2b1-75fd-4e7e-901b-495cee4ab5ad | 21 September 2020 | 06 May 2022
M0931 | Network Intrusion Prevention | course-of-action--3172222b-4983-43f7-8983-753ded4f13bc | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | If a link is being visited by a user, network intrusion prevention systems and systems designed to scan and remove malicious downloads can be used to block activity. | relationship--b1d993d5-9e7e-4043-a651-07c7b5ad5a6b | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--f15f24d2-e581-46ce-83e4-a924f572aae6 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Network segmentation can be used to isolate infrastructure components that do not require broad network access. This may mitigate, or at least alleviate, the scope of AiTM activity. | relationship--35cf6922-d48f-42ea-b7f5-f0258892bd52 | 21 September 2020 | 21 March 2023
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--b1768154-221c-48be-ab2b-549ec1eddafb | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Prevent unauthorized systems from accessing control servers or field devices containing industrial information, especially services used for common automation protocols (e.g., DNP3, OPC). | relationship--a08d85dd-a8b3-4848-94aa-941c43b6d8f2 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Restrict unauthorized devices from accessing serial comm ports. | relationship--51eca7b9-6330-48a8-badd-65ed3e9d3639 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--56672ea4-cbf0-4a3e-8aed-edcc7d33133b | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--e6e0ef82-2cb6-43fe-8f4a-b9e4d5a57b13 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | Configure internal and external firewalls to block traffic using common ports that associate to network protocols that may be unnecessary for that particular network segment. | relationship--bde941c6-2ca0-4f94-9336-027e7eee15a1 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--eac550b4-3bd2-4309-8b37-b797dd0bd8a7 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--45ee1822-71e4-4d92-976d-306561b70555 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Segment externally facing servers and services from the rest of the network with a DMZ or on separate hosting infrastructure. | relationship--fcb7733f-553d-43de-a8c6-c85a5cd65041 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Segment networks and systems appropriately to reduce access to critical system and services communications. | relationship--63323b12-86db-4b91-a701-90daf3f98f7c | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Deny direct remote access to internal systems through the use of network proxies, gateways, and firewalls. Consider a jump server or host into the DMZ for greater access control. Leverage this DMZ or corporate resources for vendor access. (Citation: Keith Stouffer May 2015) | relationship--220140ac-d927-4d86-9335-c04aa6ee3c61 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | Deny direct remote access to internal systems through the use of network proxies, gateways, and firewalls. Steps should be taken to periodically inventory internet accessible devices to determine if it differs from the expected. | relationship--33215dfa-53d0-4bd7-a15d-cec9315c7c4d | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) (Citation: N/A) | relationship--19ab6776-42de-48af-975a-568d31a3bb66 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--86d45e92-80ba-4f97-b3a3-03ad3469658b | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Segment networks and systems appropriately to reduce access to critical system and services communications. | relationship--34d4101b-b4c9-4ea3-a84d-81e84e7f5033 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--c7aac6c9-da16-46e2-8cfa-dca07a0a7562 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--8fcecf74-36df-41ab-9476-539c9ac0b339 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--671043a9-337f-411a-9ca9-3112e897ab09 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Segment and control software movement between business and OT environments by way of one directional DMZs. Web access should be restricted from the OT environment. Engineering workstations, including transient cyber assets (TCAs) should have minimal connectivity to external networks, including Internet and email, further limit the extent to which these devices are dual-homed to multiple networks. (Citation: North America Transmission Forum December 2019) | relationship--502a0b7e-048a-468a-b888-e91fde47c6eb | 12 April 2021 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--61668e93-6d9d-418d-9fbd-2d88c3a66544 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--9cca3120-c95e-4f5e-bc4b-0521ab5cc512 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--531e0589-0dad-444d-aca4-6198ba5d9fcd | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | Ensure proper network segmentation between higher level corporate resources and the control process environment. | relationship--0ff88ef7-44fd-4307-b381-2e0bc76ce83b | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Segment operational network and systems to restrict access to critical system functions to predetermined management systems. (Citation: Department of Homeland Security September 2016) | relationship--a74c14e2-eb8a-47bb-b64d-20aad9154297 | 21 September 2020 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Segment and control software movement between business and OT environments by way of one directional DMZs. Web access should be restricted from the OT environment. Engineering workstations, including transient cyber assets (TCAs) should have minimal connectivity to external networks, including Internet and email, further limit the extent to which these devices are dual-homed to multiple networks. (Citation: North America Transmission Forum December 2019) | relationship--798919d3-df8b-463f-b2be-4c1aa8089384 | 14 October 2021 | 06 May 2022
M0930 | Network Segmentation | course-of-action--1e7ccfc0-94c8-496e-8d27-032120892291 | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Segment operational assets and their management devices based on their functional role within the process. Enabling more strict isolation to more critical control and operational information within the control environment. (Citation: Karen Scarfone; Paul Hoffman September 2009) (Citation: Keith Stouffer May 2015) (Citation: Department of Homeland Security September 2016) (Citation: Dwight Anderson 2014) | relationship--206cc4c8-797e-427b-86f1-4c81df391c6e | 21 September 2020 | 06 May 2022
M0928 | Operating System Configuration | course-of-action--9a945a29-5233-4422-a9e3-3e957b0e8bce | mitigation | mitigates | T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | Configure operating systems to disable the autorun of any specific file types or drives. | relationship--98567b03-7421-4761-8caa-cbea82d89fe3 | 26 March 2024 | 26 March 2024
M0928 | Operating System Configuration | course-of-action--9a945a29-5233-4422-a9e3-3e957b0e8bce | mitigation | mitigates | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | Harden the system through operating system controls to prevent the known or unknown use of malicious removable media. | relationship--604a9bf0-81a3-425b-9005-779c4f0f749d | 21 September 2020 | 06 May 2022
M0809 | Operational Information Confidentiality | course-of-action--99c746d7-a08a-4169-94f9-b8c0dad716fa | mitigation | mitigates | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | Example mitigations could include minimizing its distribution/storage or obfuscating the information (e.g., facility coverterms, codenames). In many cases this information may be necessary to support critical engineering, maintenance, or operational functions, therefore, it may not be feasible to implement. | relationship--69576d3c-d0e8-459e-9f2e-0b9c560b2e04 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel. | relationship--52855d5d-e835-470f-a675-751c2779c861 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Provide an alternative method for alarms to be reported in the event of a communication failure. | relationship--c9395e2a-afaf-427c-bcb2-ae663d72c05c | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Provide an alternative method for sending critical commands message to outstations, this could include using radio/cell communication to send messages to a field technician that physically performs the control function. | relationship--0c9ed09d-4ce3-4e65-845a-c21dcc5d956f | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Provide an alternative method for sending critical report messages to operators, this could include using radio/cell communication to obtain messages from field technicians that can locally obtain telemetry and status data. | relationship--2c8dd182-e0a1-469d-aa65-7a1f734d9b46 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | Ensure devices have an alternative method for communicating in the event that a valid COM port is unavailable. | relationship--7d0ec383-4c5d-474d-9262-3f3c0d6c05b1 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--2089201c-c1c6-4d92-a737-a6499e26ee7f | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--18ef2d69-d11a-4d31-a803-da989c4073f7 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--52c7176b-431d-44a6-8c03-7c15a8cf6ce1 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--8b17ad46-b0cc-4766-9cae-eba32260d468 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | Provide operators with redundant, out-of-band communication to support monitoring and control of the operational processes, especially when recovering from a network outage (Citation: National Institute of Standards and Technology April 2013). Out-of-band communication should utilize diverse systems and technologies to minimize common failure modes and vulnerabilities within the communications infrastructure. For example, wireless networks (e.g., 3G, 4G) can be used to provide diverse and redundant delivery of data. | relationship--ecf39e19-439f-4e9a-97c2-673ce4eb0a1a | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel. | relationship--520aad6a-2483-45bc-a172-2417137f6ca0 | 21 September 2020 | 06 May 2022
M0810 | Out-of-Band Communications Channel | course-of-action--b11cad63-ef30-4eb8-af0d-6cc46eef3f3e | mitigation | mitigates | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | Utilize out-of-band communication to validate the integrity of data from the primary channel. | relationship--58cb4cb5-4b0f-4ce0-b3f9-5deb9de31c52 | 21 September 2020 | 06 May 2022
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | Applications and appliances that utilize default username and password should be changed immediately after the installation, and before deployment to a production environment.(Citation: CISA June 2013) | relationship--53af6987-21bb-46fd-bf85-e3eeaa74de1a | 30 March 2023 | 30 March 2023
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | Review vendor documents and security alerts for potentially unknown or overlooked default credentials within existing devices | relationship--33486e89-f0f4-4507-9f13-48a8f22c8ac8 | 21 September 2020 | 06 May 2022
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Set and enforce secure password policies for accounts. | relationship--98f1d575-a975-42ae-8b00-2c9e22d560d5 | 21 September 2020 | 06 May 2022
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Enforce strong password requirements to prevent password brute force methods for lateral movement. | relationship--5212f36b-216f-4e32-8b64-3b4c94dfada5 | 10 April 2021 | 06 May 2022
M0927 | Password Policies | course-of-action--5d97c693-e054-48ba-a3a3-eaf6942dfb65 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Applications and appliances that utilize default username and password should be changed immediately after the installation, and before deployment to a production environment. (Citation: CISA June 2013) | relationship--a1383f2a-2ee2-47df-a661-8904a7535e0c | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Minimize permissions and access for service accounts to limit the information that may be impacted by malicious users or software. (Citation: National Institute of Standards and Technology April 2013) | relationship--e8eaac2d-a4bf-408f-b24f-14471db7059b | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Minimize permissions and access for service accounts to limit the information that may be exposed or collected by malicious users or software. (Citation: National Institute of Standards and Technology April 2013) | relationship--ba010007-6dde-4c9d-8452-69527cd1c2ba | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Use least privilege for service accounts. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--bc3744d6-9275-4d91-8888-16d5f4d5187b | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Minimize permissions and access for service accounts to limit impact of exploitation. (Citation: Keith Stouffer May 2015) | relationship--a78e727c-8e42-448c-beb4-463804e18be0 | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Restrict root or administrator access on user accounts to limit the ability to capture promiscuous traffic on a network through common packet capture tools. (Citation: National Institute of Standards and Technology April 2013) | relationship--26fdd07e-d194-4f8e-a9af-d5b2f1d0222e | 21 September 2020 | 06 May 2022
M0926 | Privileged Account Management | course-of-action--622fe4d4-0e8e-4d17-9c25-6c9cef1f15d5 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Audit domain and local accounts and their permission levels routinely to look for situations that could allow an adversary to gain system wide access with stolen privileged account credentials. (Citation: Microsoft May 2017) (Citation: Microsoft August 2018)These audits should also identify if default accounts have been enabled, or if new local accounts are created that have not be authorized. Follow best practices for design and administration of an enterprise network to limit privileged account use across administrative tiers. (Citation: Microsoft February 2019) | relationship--111f437a-c67d-40e4-9515-7e9b22e65eff | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | Retain cold-standby or replacement hardware of similar models to ensure continued operations of critical functions if the primary system is compromised or unavailable. (Citation: M. Rentschler and H. Heine) | relationship--cb6d67c0-33ba-4c49-ae70-d0e4f0f68794 | 30 March 2023 | 30 March 2023
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--99ec0a8e-4a4f-427c-89db-163e4b206021 | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--e852e64c-b5e0-4e7f-a189-bbc7aa7932c7 | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system is compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--afb0b60e-e604-4b96-abb9-57fdce4e5108 | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--7041d8e5-3b74-402a-86b3-fd59def80632 | 21 September 2020 | 06 May 2022
M0811 | Redundancy of Service | course-of-action--f0f5c87a-a58d-440a-b3b5-ca679d98c6dd | mitigation | mitigates | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | Hot-standbys in diverse locations can ensure continued operations if the primarily system are compromised or unavailable. At the network layer, protocols such as the Parallel Redundancy Protocol can be used to simultaneously use redundant and diverse communication over a local network. (Citation: M. Rentschler and H. Heine) | relationship--8ecf5eac-7767-411b-b54a-b374ea51b9e9 | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to impact data storage. (Citation: National Institute of Standards and Technology April 2013) | relationship--21b6ec9c-8779-49db-bf19-90e81893a6e4 | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Protect files with proper permissions to limit opportunities for adversaries to interact and collect information from databases. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--86f1655a-db46-4d49-9051-6653da83eb13 | 21 September 2020 | 30 March 2023
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to interact and collect information from the local system. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--94654460-b115-4056-beb1-e982ed33437b | 30 March 2023 | 30 March 2023
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to remove indicators of their activity on the system. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--92d1fd4f-6cc7-4db5-82f8-f8caa5ff59f0 | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | Use file system access controls to protect system and application folders. | relationship--f703f8b2-b6b9-41f3-a551-6bb3647c45cc | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | Ensure permissions restrict project file access to only engineer and technician user groups and accounts. | relationship--42ab7d24-8286-4a7a-8cd7-02e54a80e13f | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Ensure proper process and file permissions are in place to inhibit adversaries from disabling or interfering with critical services. | relationship--6833d534-9cbb-4b9f-85b6-93d3d2d6faca | 21 September 2020 | 06 May 2022
M0922 | Restrict File and Directory Permissions | course-of-action--f9fcb3ec-6de0-4559-8cd9-ef1c0c7d1971 | mitigation | mitigates | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | Protect files stored locally with proper permissions to limit opportunities for adversaries to interact and collect information from databases. (Citation: Keith Stouffer May 2015) (Citation: National Institute of Standards and Technology April 2013) | relationship--2e5f338d-92c4-4647-8fef-7c901ff774f5 | 21 September 2020 | 06 May 2022
M0944 | Restrict Library Loading | course-of-action--2ab9fc6d-3cf6-4d7b-85f1-3ad6949233b3 | mitigation | mitigates | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | Restrict the use of untrusted or unknown libraries, such as remote or unknown DLLs. | relationship--04882fef-2a6b-40d0-a101-da9c76a3572e | 21 September 2020 | 06 May 2022
M0924 | Restrict Registry Permissions | course-of-action--3222a807-521b-4a1a-aa13-f1cda45734b3 | mitigation | mitigates | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Ensure proper registry permissions are in place to inhibit adversaries from disabling or interfering with critical services. | relationship--0e4f272b-d744-4feb-9f3f-c24c3598538f | 21 September 2020 | 06 May 2022
M0921 | Restrict Web-Based Content | course-of-action--143b4398-3222-480a-b6a4-e131bc2d3144 | mitigation | mitigates | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Restrict browsers to limit the capabilities of malicious ads and Javascript. | relationship--fcd3fdbf-4909-48ab-85c4-ce4b34172eb0 | 21 September 2020 | 06 May 2022
M0921 | Restrict Web-Based Content | course-of-action--143b4398-3222-480a-b6a4-e131bc2d3144 | mitigation | mitigates | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Consider restricting access to email within critical process environments. Additionally, downloads and attachments may be disabled if email is still necessary. | relationship--c195a0e9-d46c-487f-9a96-b138e9ca05d2 | 21 September 2020 | 06 May 2022
M0921 | Restrict Web-Based Content | course-of-action--143b4398-3222-480a-b6a4-e131bc2d3144 | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | If a link is being visited by a user, block unknown or unused files in transit by default that should not be downloaded or by policy from suspicious sites as a best practice to prevent some vectors, such as .scr, .exe, .pif, .cpl, etc. Some download scanning devices can open and analyze compressed and encrypted formats, such as zip and rar that may be used to conceal malicious files. | relationship--1aa02c37-973e-46bd-ab45-609463e514e9 | 21 September 2020 | 06 May 2022
M0920 | SSL/TLS Inspection | course-of-action--6a02e38a-9629-40c0-8c7d-e98e3470315c | mitigation | mitigates | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | If it is possible to inspect HTTPS traffic, the captures can be analyzed for connections that appear to be domain fronting. | relationship--20a0d820-59ef-42fc-9f56-7a93d1ce7a84 | 21 September 2020 | 06 May 2022
M0812 | Safety Instrumented Systems | course-of-action--da44255d-85c5-492c-baf3-ee823d44f848 | mitigation | mitigates | T0879 | Damage to Property | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | technique | Ensure that all SIS are segmented from operational networks to prevent them from being targeted by additional adversarial behavior. | relationship--d1d98f8c-aea2-4f06-9b0d-c543ed42c6a4 | 21 September 2020 | 06 May 2022
M0812 | Safety Instrumented Systems | course-of-action--da44255d-85c5-492c-baf3-ee823d44f848 | mitigation | mitigates | T0880 | Loss of Safety | attack-pattern--5fa00fdd-4a55-4191-94a0-564181d7fec2 | technique | Ensure that all SIS are segmented from operational networks to prevent them from being targeted by additional adversarial behavior. | relationship--0ffdee1a-1e83-4506-aba2-38c55812abb3 | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--758d5818-f919-4a6b-9dc2-a212595a11bd | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | To protect against AiTM, authentication mechanisms should not send credentials across the network in plaintext and should also implement mechanisms to prevent replay attacks (such as nonces or timestamps). Challenge-response based authentication techniques that do not directly send credentials over the network provide better protection from AiTM. | relationship--71e9230d-eec8-4ce1-bc96-9288bacc8b13 | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | Devices should authenticate all messages between master and outstation assets. | relationship--be950e87-80ac-49ea-810a-553c7f72151b | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--7d5759cd-890e-4ec5-b92b-aba225d52960 | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions. | relationship--107d9a23-991b-44f5-97f6-7f6983c7013a | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions. | relationship--f862418a-e7b4-4783-8949-7145f3dee665 | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--5d4f6aff-650c-45fe-a9d8-2080d3ea02d7 | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--26e58427-a2bd-4e77-9939-16ef60a072e7 | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | Devices should authenticate all messages between master and outstation assets. | relationship--984992e3-0407-406a-b8dd-c114d8b2d9a2 | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions. | relationship--028a3bcc-f299-4061-a0f2-8da85e0a3c81 | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | Authenticate connections from software and devices to prevent unauthorized systems from accessing protected management functions. | relationship--06c663f8-fcf1-47eb-ab79-284e93eafa6b | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | All communication sessions to remote services should be authenticated to prevent unauthorized access. | relationship--4211c12a-57cf-4ebb-910a-6af7aa09cf34 | 12 April 2021 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | Devices should authenticate all messages between master and outstation assets. | relationship--0f8a6c14-1050-404a-bb6e-4fe107d5b6cd | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | Devices should authenticate all messages between master and outstation assets. | relationship--088580e9-ccea-426e-9411-c1de60de650d | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Authenticate connections fromsoftware and devices to prevent unauthorized systems from accessing protected management functions. | relationship--bcaa4f7e-2e84-4bbb-9fb7-ca8fb003108f | 21 September 2020 | 21 March 2023
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Devices should authenticate all messages between master and outstation assets. | relationship--bbf297d3-0c3c-44be-b780-332bac17b0ba | 21 September 2020 | 06 May 2022
M0813 | Software Process and Device Authentication | course-of-action--72e46e53-e12d-4106-9c70-33241b6ed549 | mitigation | mitigates | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | Ensure wireless networks require the authentication of all devices, and that all wireless devices also authenticate network infrastructure devices (i.e., mutual authentication). For defense-in-depth purposes, utilize VPNs or ensure that application-layer protocols also authenticate the system or device. Use protocols that provide strong authentication (e.g., IEEE 802.1X), and enforce basic protections, such as MAC filtering, when stronger cryptographic techniques are not available. | relationship--3f335e8f-68da-4b06-9d96-f371ddaf23e6 | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | Statically defined ARP entries can prevent manipulation and sniffing of switched network traffic, as some AiTM techniques depend on sending spoofed ARP messages to manipulate network host's dynamic ARP tables. | relationship--808174b7-3ab0-45b5-963e-5c10dd749e3c | 21 September 2020 | 21 March 2023
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections. | relationship--5d33de22-35b0-47fa-bc63-f984522340b7 | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections. | relationship--f951d934-d555-45e9-a564-27b84518cae4 | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | Unauthorized connections can be prevented by statically defining the hosts and ports used for automation protocol connections. | relationship--139bb9e7-e5fd-4366-b2e6-4f74a73ec984 | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | Statically defined ARP entries can prevent manipulation and sniffing of switched network traffic, as some AiTM techniques depend on sending spoofed ARP messages to manipulate network host's dynamic ARP tables. | relationship--df6da4ec-cbe8-4f93-a41f-3726a9491938 | 21 September 2020 | 21 March 2023
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | ICS environments typically have more statically defined devices, therefore minimize the use of both IT discovery protocols (e.g., DHCP, LLDP) and discovery functions in automation protocols. (Citation: D. Parsons and D. Wylie September 2019) (Citation: Colin Gray) Examples of automation protocols with discovery capabilities include OPC UA Device Discovery (Citation: Josh Rinaldi April 2016), BACnet (Citation: Aditya K Sood July 2019), and Ethernet/IP. (Citation: Langner November 2018) | relationship--b2defaaf-625d-416e-8a9d-8be6d89bacdc | 21 September 2020 | 06 May 2022
M0814 | Static Network Configuration | course-of-action--52c7a1a9-3a78-4528-a44f-cd7b0fa3541a | mitigation | mitigates | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | ICS environments typically have more statically defined devices, therefore minimize the use of both IT discovery protocols (e.g., DHCP, LLDP) and discovery functions in automation protocols. (Citation: D. Parsons and D. Wylie September 2019) (Citation: Colin Gray) Examples of automation protocols with discovery capabilities include OPC UA Device Discovery (Citation: Josh Rinaldi April 2016), BACnet (Citation: Aditya K Sood July 2019), and Ethernet/IP. (Citation: Langner November 2018) | relationship--74ec9ce5-3155-488c-ae56-570c47a1d207 | 13 April 2021 | 06 May 2022
M0817 | Supply Chain Management | course-of-action--ac8f3492-7fbb-4a0a-b0b4-b75ec676136c | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | A supply chain management program should include methods the assess the trustworthiness and technical maturity of a supplier, along with technical methods (e.g., code-signing, bill of materials) needed to validate the integrity of newly obtained devices and components. Develop procurement language that emphasizes the expectations for suppliers regarding the artifacts, audit records, and technical capabilities needed to validate the integrity of the devices supply chain. (Citation: Robert A. Martin January 2021) | relationship--c8a40335-90d6-496a-b4f9-1cc93d3fffc6 | 12 April 2021 | 06 May 2022
M0919 | Threat Intelligence Program | course-of-action--d48b79b2-076d-483e-949c-0d38aa347499 | mitigation | mitigates | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization. | relationship--08302021-aacf-428f-a0ce-e1034d925fb0 | 21 September 2020 | 06 May 2022
M0919 | Threat Intelligence Program | course-of-action--d48b79b2-076d-483e-949c-0d38aa347499 | mitigation | mitigates | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization. | relationship--f40cc6f5-111c-418f-aa84-50d920fa6c48 | 13 April 2021 | 06 May 2022
M0919 | Threat Intelligence Program | course-of-action--d48b79b2-076d-483e-949c-0d38aa347499 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Develop a robust cyber threat intelligence capability to determine what types and levels of threat may use software exploits and 0-days against a particular organization. | relationship--5914a482-dbb7-429d-96f3-77f0588ac12d | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | Ensure all browsers and plugins are kept updated to help prevent the exploit phase of this technique. Use modern browsers with security features enabled. | relationship--1a40cec9-47c3-404e-b039-b7ae83ffaf68 | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Regularly scan externally facing systems for vulnerabilities and establish procedures to rapidly patch systems when critical vulnerabilities are discovered through scanning and public disclosure. | relationship--6f2c2043-6487-467a-bb49-e8cd2509ae9f | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers. | relationship--97c5b388-518a-46ec-b2b0-41bfa6a83204 | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers. | relationship--91f29477-2ff6-4dbf-bf68-c8825a938851 | 13 April 2021 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Update software regularly by employing patch management for internal enterprise endpoints and servers. | relationship--e0d101cc-1284-4e88-82d6-227fe5d19d8a | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | A patch management process should be implemented to check unused dependencies, unmaintained and/or previously vulnerable dependencies, unnecessary features, components, files, and documentation. | relationship--03d44496-7a15-4e23-820f-b6f1079dbbd3 | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | Patch the BIOS and EFI as necessary. | relationship--a75ddacf-e87e-4a99-83f2-618486473163 | 21 September 2020 | 06 May 2022
M0951 | Update Software | course-of-action--97f33c84-8508-45b9-8a1d-cac921828c9e | mitigation | mitigates | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | Update software on control network assets when possible. If feasible, use modern operating systems and software to reduce exposure to known vulnerabilities. | relationship--b8edcf0a-ec53-4203-b3ad-2cc734a1f1dd | 14 October 2021 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Ensure users and user groups have appropriate permissions for their roles through Identity and Access Management (IAM) controls to prevent misuse. Implement user accounts for each individual that may access the repositories for role enforcement and non-repudiation of actions. | relationship--b9632b4d-43c3-4bfa-88e0-629245acb8eb | 21 September 2020 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | Consider utilizing jump boxes for external remote access. Additionally, dynamic account management may be used to easily remove accounts when not in use. | relationship--a7fbe555-a61b-4b93-bfb2-8e0dd0d6323e | 21 September 2020 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | Limit privileges of user accounts and groups so that only designated administrators or engineers can interact with alarm management and alarm configuration thresholds. | relationship--7fdaa9be-aecf-459f-b028-7c35dc8b6451 | 21 September 2020 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | Limit the accounts that may use remote services. Limit the permissions for accounts that are at higher risk of compromise; for example, configure SSH so users can only run specific programs. | relationship--ae10e97a-90ac-498b-8601-01081dc4af8b | 12 April 2021 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Limit privileges of user accounts and groups so that only authorized administrators can change service states and configurations. | relationship--01b4a92f-da42-4dfa-8d59-53709b65940e | 21 September 2020 | 06 May 2022
M0918 | User Account Management | course-of-action--e57ebc6d-785f-40c8-adb1-b5b5e09b3b48 | mitigation | mitigates | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | Ensure users and user groups have appropriate permissions for their roles through Identity and Access Management (IAM) controls. Implement strict IAM controls to prevent access to systems except for the applications, users, and services that require access. Implement user accounts for each individual for enforcement and non-repudiation of actions. | relationship--1fc147bd-d6ab-4beb-908b-0fbe8e125b76 | 21 September 2020 | 06 May 2022
M0917 | User Training | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | mitigation | mitigates | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | Develop and publish policies that define acceptable information to be stored in repositories. | relationship--f497fd3e-8f05-4db2-97cc-48a8d35a8827 | 21 September 2020 | 06 May 2022
M0917 | User Training | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | mitigation | mitigates | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | Develop and publish policies that define acceptable information to be stored on local systems. | relationship--b48a9fea-26a5-473c-9a5d-fcc3531e1fd3 | 30 March 2023 | 30 March 2023
M0917 | User Training | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | mitigation | mitigates | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | Users can be trained to identify social engineering techniques and spearphishing emails. | relationship--81ca994a-b350-424d-8f39-a0b64aa76260 | 21 September 2020 | 06 May 2022
M0917 | User Training | course-of-action--dc61c280-c29d-44e5-a960-c0dd1623d2ba | mitigation | mitigates | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Use user training as a way to bring awareness to common phishing and spearphishing techniques and how to raise suspicion for potentially malicious events. | relationship--71c9db9c-6f0c-4e33-a20a-dcd5b791a49a | 21 September 2020 | 06 May 2022
M0818 | Validate Program Inputs | course-of-action--1cbcceef-3233-4062-aa86-ec91afe39517 | mitigation | mitigates | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | Devices and programs should validate the content of any remote parameter changes, including those from HMIs, control servers, or engineering workstations.(Citation: PLCTop20 Mar 2023) | relationship--f86bde61-c4ec-4d40-9768-32e9b52c1702 | 22 March 2023 | 22 March 2023
M0818 | Validate Program Inputs | course-of-action--1cbcceef-3233-4062-aa86-ec91afe39517 | mitigation | mitigates | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Devices and programs that receive command messages from remote systems (e.g., control servers) should verify those commands before taking any actions on them. | relationship--07c0e166-f05e-413f-8f3e-f487317c9626 | 22 March 2023 | 22 March 2023
M0916 | Vulnerability Scanning | course-of-action--de0bc375-50e1-4e26-a342-a8ff8c9d3037 | mitigation | mitigates | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | Regularly scan externally facing systems for vulnerabilities and establish procedures to rapidly patch systems when critical vulnerabilities are discovered through scanning and public disclosure. | relationship--968830b7-ee80-4a6e-96a4-9fc70470e4a9 | 21 September 2020 | 06 May 2022
M0916 | Vulnerability Scanning | course-of-action--de0bc375-50e1-4e26-a342-a8ff8c9d3037 | mitigation | mitigates | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | Regularly scan the internal network for available services to identify new and potentially vulnerable services. | relationship--1f87378c-49fb-4da5-8ed3-3672633d3713 | 21 September 2020 | 06 May 2022
M0916 | Vulnerability Scanning | course-of-action--de0bc375-50e1-4e26-a342-a8ff8c9d3037 | mitigation | mitigates | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | Implement continuous monitoring of vulnerability sources. Also, use automatic and manual code review tools. (Citation: OWASP) | relationship--c67e3535-69a9-4234-8170-4ad6efc632b7 | 21 September 2020 | 06 May 2022
M0815 | Watchdog Timers | course-of-action--98aa0d61-fc9d-4b2d-8f18-b25d03549f53 | mitigation | mitigates | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | System and process restarts should be performed when a timeout condition occurs. | relationship--5d0a7979-0420-4fd1-b5ad-cb5565cbdf9d | 21 September 2020 | 06 May 2022
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--128de3f9-df58-4122-9523-0ac65a6ebf71 | 29 September 2023 | 29 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--e5c9aacb-51e3-41d3-995d-9e6ed04a2454 | 02 October 2023 | 02 October 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--0dbf48f3-4579-4ca2-aceb-19d3e0449136 | 29 September 2023 | 29 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--c4b036ee-be86-48cb-9f01-ab8f78e5bb37 | 28 September 2023 | 28 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--f9907fb1-976b-4f51-ac13-b45f2ff9452b | 28 September 2023 | 28 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--ba943eeb-5673-44b5-acbf-1cddc2fefb1a | 28 September 2023 | 28 September 2023
T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--b59a96e4-bd70-4459-9609-66563bccd9c3 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--69cf4015-fae1-47f6-9253-1f99209288a5 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--da987131-bf37-4730-9914-323879d2b5c3 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--ab844cd2-0f56-44f9-9838-cd5f04d75f3e | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--327f65bc-8a33-4dbb-88d4-714a9e42442b | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--eb5310c6-7500-4b16-8ca7-6678c6232001 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--745b5268-f2b3-499c-a6a4-63d7e8667ff7 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--01335508-22bb-4185-a7e2-49ec9bee6423 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--0a421699-f013-49f4-9d9f-01d95d210510 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--df80e2b6-5672-4f26-a19c-a394f3731f24 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--eebae2f3-aaa1-4410-8b75-db5bdac1d4d6 | 28 September 2023 | 28 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--02117d44-46d2-41f0-a5fb-ba303e6ee124 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--79235599-e23f-43cb-9c56-1eb22b7c4664 | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--8fe2bc4c-e9f7-430d-84d5-e3d603141dcb | 29 September 2023 | 29 September 2023
T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--a91295dc-b381-4dc9-9384-9f9949066778 | 29 September 2023 | 29 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--305866af-1f36-49e0-a57d-d5faaf29011c | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--11a82651-4d69-4738-89c6-17d0243cbbb0 | 29 September 2023 | 29 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--b0945f9b-5608-472e-ad70-7b42c3e062a1 | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--0ef1e408-8ebb-4b28-b619-02914b7bae29 | 29 September 2023 | 29 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--45d14170-7f7b-4e08-b53f-42fa4a3a04d9 | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b3aab26c-09c6-4264-af2a-5df260d3d8e2 | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--9ffbf620-8e1f-4542-a271-9a3692db9a47 | 28 September 2023 | 28 September 2023
T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--76537fd7-5782-4a8d-9b54-117b168a4306 | 29 September 2023 | 29 September 2023
T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--544e996c-0bdc-42b2-91af-14c27d4213b9 | 28 September 2023 | 28 September 2023
T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--ff107632-751b-4efb-86bd-af670b48d35d | 28 September 2023 | 28 September 2023
T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--685249f9-e51a-4914-8b7f-09679e04198b | 28 September 2023 | 28 September 2023
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--630eb861-eb37-4258-9dbd-87789df2257a | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--fd309395-8fcc-402c-9227-90ac897fd602 | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--982d0b4f-274a-4738-9262-57fc80d468f9 | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--fcba6a58-72b0-4d54-a887-740624e22f6f | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--a72c212f-6d4f-4c5d-873d-afa42021024c | 26 March 2024 | 26 March 2024
T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--6eafa3e9-f53f-43b5-ac24-1415b05b537f | 26 March 2024 | 26 March 2024
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--788a2994-f3fd-4ac4-9ef3-06a72a4e1631 | 28 September 2023 | 28 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--17d5794d-dcd5-4e0f-87e4-87d41c24b5fa | 02 October 2023 | 02 October 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--a46f722e-4399-4aa6-b0a9-61fae9d0bf63 | 29 September 2023 | 29 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--0951222a-42d1-4635-bb12-5285bc6500e0 | 28 September 2023 | 28 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--8f947e00-2579-4120-a8b0-d466e59fac1a | 28 September 2023 | 28 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--9a3e771d-d84f-4f2a-baf9-4478abdbdbcf | 28 September 2023 | 28 September 2023
T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--5677e801-bd49-404b-b54a-6b00da52530c | 29 September 2023 | 29 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--86e7a6d1-baa5-4a8d-9ba8-302fb0d72f9c | 28 September 2023 | 28 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--afe18ec4-b5b8-43f7-b9e9-64a579b4b4e1 | 29 September 2023 | 29 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--31d7e048-92fc-4b63-b0d5-28b64b39797a | 02 October 2023 | 02 October 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--4f4e2e9e-6f9a-4c9c-af2b-4db4ec444c93 | 29 September 2023 | 29 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--cd54b7ba-c96c-49c8-90d2-15677efb8fe2 | 28 September 2023 | 28 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--483719ad-c973-4210-b059-14e87dbd45f8 | 28 September 2023 | 28 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--908e3fa1-e2b9-475e-b72d-06343a65a3c6 | 28 September 2023 | 28 September 2023
T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--eff19f74-4940-4c8e-a3b3-b3c16fe3f5e0 | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--4ad48410-efd9-41c0-ac59-e4343d3b9198 | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--ab5c9a38-3140-43b6-bcf4-6197a116cd0b | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--6b54f354-9059-4366-8077-87360c4db2ab | 02 October 2023 | 02 October 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--edfa4bcb-6304-42df-b7c6-8caf480c66f2 | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--66738beb-0a33-4d70-baec-8307b5b34f80 | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--9ba76ea3-9ebb-49d7-803a-5cf2deef6875 | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--f4afb180-4b30-4ed1-b094-3d74d8fd0cf1 | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--ac933d76-8207-4bf7-add2-92b60cf3044b | 28 September 2023 | 28 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--ed8b97e2-5966-4844-a636-524541a46e43 | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--2fe222c4-cc81-473d-956e-235e2961a5c3 | 29 September 2023 | 29 September 2023
T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--01d002a2-696a-4e22-b227-b0b32f54eaf0 | 29 September 2023 | 29 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--ccbb44ad-2220-4260-99ce-9142c44fc797 | 28 September 2023 | 28 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c1d77f83-23ec-4128-afd1-ed8ea12281a2 | 29 September 2023 | 29 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--076bfea6-309e-4804-a147-dffe93983481 | 28 September 2023 | 28 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--ae4e86c6-4bbb-4aba-80fc-c20a8f3d63dc | 28 September 2023 | 28 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--eae674f9-10a2-41e6-9cd3-205af8e69d53 | 28 September 2023 | 28 September 2023
T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--edaa6f5c-1b59-4ecb-a20f-716a61cdaccb | 29 September 2023 | 29 September 2023
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--23851bda-49de-4f35-979f-c4e6b5742389 | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--24793eaf-f0d8-4baf-ba3d-900b87cf464d | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--525d0a51-bbf9-4cda-aec9-562bb05bd3a0 | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--2f7c49a0-89fe-4d18-915c-c321868d47bd | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c596f45a-ad65-4673-b316-05378175f35e | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--cbc65a60-3b40-4ecf-a10d-8ef1be72568d | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--0e191d66-fe38-4f28-ad82-6922bd6bcc81 | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--7dd11d5e-1c1c-4f94-b4bf-4fd59988539b | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--6067c069-8e93-4bf0-bb49-97538d55c3de | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--e4c62e59-d14e-4cbc-a4a9-4f64bd523d5a | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--c8222300-6c5e-42d6-ae67-3595407b89fd | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--16c7240e-0559-4c49-9003-1bfe97074252 | 09 April 2024 | 09 April 2024
T0892 | Change Credential | attack-pattern--fab8fc7d-f27f-4fbb-9de6-44740aade05f | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--c4dd7251-ed87-4629-86b5-090e52a82df2 | 09 April 2024 | 09 April 2024
T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--e8ef9bb9-1335-4418-b788-f8220dbbe4c8 | 28 September 2023 | 28 September 2023
T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--e83a79df-2555-4b2f-9ade-b9ed2689ae42 | 29 September 2023 | 29 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--0e263b73-a033-4fac-9d6d-076ab8f8b954 | 29 September 2023 | 29 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--296375b0-817d-4f42-afe1-4308f5edf973 | 28 September 2023 | 28 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--0a5002d3-cf0d-4e26-9fc4-8faff7f6578a | 29 September 2023 | 29 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--d1a97502-b41d-40a8-aff5-13367fefc642 | 28 September 2023 | 28 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--033b4401-261f-498b-89f3-2bad9ff5907a | 29 September 2023 | 29 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--58a95ec2-0079-4d58-a7ed-02664c1095ba | 28 September 2023 | 28 September 2023
T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--5b14c813-09e2-4709-ab42-94830cf9538c | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--fac4bc88-af9b-4eec-b041-e4138b49c3c0 | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--fe22f626-ddf3-4d5e-97d1-058878d7830f | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--d5e908f9-eea1-4e55-a406-f24c5dc74b2d | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--2159458f-87fc-4479-81f4-a2521a378221 | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--1a3ecee5-0237-4e01-8f02-90092c15a2f0 | 02 October 2023 | 02 October 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--df7b521e-4496-432f-a61d-3094d0c7bc23 | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--5ee01089-2ab6-4cf5-a39d-adf72666eceb | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--d3564f1f-8637-4878-a66a-3e8ea46f7a72 | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--4a7340fc-0eec-4459-a491-952d736b79ef | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--ee72cc27-2e78-47c4-8786-1351f9bcee97 | 28 September 2023 | 28 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--106530e1-375a-4ac4-befb-8297b3b05610 | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--a3f258ea-6d4d-4b0e-8ff2-b91f49dfd4d7 | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--413c1c41-6ef9-413b-a75a-e67f1668b3db | 29 September 2023 | 29 September 2023
T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--b84e1473-f370-42ad-ac3b-7caf3c8cd00e | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--a1d99bbc-8d7c-4263-a909-95a9507b43c3 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--b289c971-3fb7-4c3c-b3d6-cf2702b9384a | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--fc189fa0-1235-46ac-a802-f226dc0ec4e1 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--bc3a0b1f-f0ec-466f-8cad-8f47b07764c9 | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--65e25631-05de-4ce2-88cc-52f91cfbdaf2 | 02 October 2023 | 02 October 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--652c1e77-cfea-4452-9762-5ba16f874119 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--f8456c9b-a4a5-4f13-94e3-54c787b21089 | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--2aaa6840-47fc-455c-9b19-1d27c3afccbe | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--d48894cb-457e-4a81-82b4-2d735aea5128 | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--07e06d21-e666-4274-838a-ef9996fdc0cd | 28 September 2023 | 28 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--2289f005-7863-4af5-b681-cdfc03d3f111 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--14c73603-a6d2-4a8d-9904-0f8249aaa495 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--f61944a4-fef5-4989-bc3d-68f86e65d7d4 | 29 September 2023 | 29 September 2023
T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--a93ba793-24dd-47dd-b32c-4c3016124c90 | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--38bda770-c470-4358-a9ad-a5b39bec026b | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--21aa6331-3419-4049-b180-8349b71e1f2a | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--938ff1d4-acce-4e4e-8a9c-be62799dff8e | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f92764db-a880-4726-9d28-a035170f790c | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--ac63d227-ff8a-43b8-81ef-ec4c046c4291 | 02 October 2023 | 02 October 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--edccbe1f-a07a-405e-9b9a-b247ce3dcc9b | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--fadbdca3-3c98-497c-a156-e53b89664359 | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--b21e0340-976d-44b2-94ae-f777199993c6 | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--d9fa7d68-a07c-4cf0-bb01-14e2c70c21d5 | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--16ac0172-02d1-4fda-99c0-61f1cef7dc4b | 28 September 2023 | 28 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--18af193c-160a-4cae-9078-4d69de5c2347 | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--5201c576-70a5-4b32-8dfd-dd8ac86f096c | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--3dd15958-b159-4d01-b3c2-37bdf9b417b5 | 29 September 2023 | 29 September 2023
T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--81806f43-c9aa-486e-8032-4e4665ba0d39 | 29 September 2023 | 29 September 2023
T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--8474e6ef-39c4-4ecc-ba5a-cbd9b32b5c65 | 28 September 2023 | 28 September 2023
T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--0b6cd19f-ee13-4224-9e22-f8a9e626d98f | 28 September 2023 | 28 September 2023
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--ca225ea0-e813-4205-98db-707b474ae24f | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--484b0873-59ef-41a3-b33d-b3fb41a2c957 | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--66d8f3d7-68e0-48a0-a563-4746922080fc | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--9537d9c9-ba0d-42d9-b97d-3b28bfe265e6 | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--f7d672f6-993b-4036-961d-f6e22e94446c | 09 April 2024 | 09 April 2024
T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--e41a04fe-a142-4294-a9f2-576214e1f985 | 09 April 2024 | 09 April 2024
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--c2168fe8-be19-4df5-808e-ed87c9c0e1c5 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--d648b3c7-77d2-42f3-a367-620621b714ab | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--eac205a6-271b-4a86-acf3-6f4ddefb82c4 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f10611e9-4812-4780-a1d5-0ad537dd95fb | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--f19c34b2-ef3a-4581-b604-6639f501e32f | 02 October 2023 | 02 October 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c6a05c20-02d4-42ce-ad5c-280c604e13d8 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--956bbc7f-82c2-4097-8b7b-1e9d732c532d | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--688d2041-5c8b-47e0-86e1-a8d16134bdb1 | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--0cab29c6-d196-47b0-8621-10ac3c8a95d8 | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--600f0115-94e3-49bf-afa6-0180b3367b94 | 28 September 2023 | 28 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--bf8e68fe-1969-48d1-be0e-ec742378748d | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--aff2fb40-9ef5-42c9-bc7a-4939b509fbf1 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--f61e474c-d7be-411e-a30e-0a1ef872fe51 | 29 September 2023 | 29 September 2023
T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--99fa6d92-0c41-44ed-bd30-dd0413785883 | 29 September 2023 | 29 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--eeeb83cb-0a8a-412b-aae2-aede7c43d8e8 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--2dc39956-05d1-4dd5-86db-cb70568d73fe | 29 September 2023 | 29 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--4c53b294-973f-4cc2-a781-6c86b8f1c962 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--39452123-574f-4f3a-95ec-a90170a3d7eb | 02 October 2023 | 02 October 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--8530c1ea-fe9f-4b04-be34-7404d5e30e75 | 29 September 2023 | 29 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--968fd463-fec4-4b2d-b3c9-950d8471b9a8 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--12fdacea-28f7-4113-ae67-0b19e1ab5e36 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b7a9bff5-2e15-4d3d-ac88-84af1239a586 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--ca13a117-aae0-4802-878b-c09f4a04dd31 | 28 September 2023 | 28 September 2023
T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--7bb1dbec-7314-479a-9496-86f8e25041eb | 29 September 2023 | 29 September 2023
T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--2c79920a-f2d1-4114-a1df-924835da645c | 28 September 2023 | 28 September 2023
T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--97e20860-29d9-4738-a9a8-6cc3e4db23f1 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--d1bd77d4-9f1a-41ee-bf64-0aa7438e6896 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--ede2b798-2f39-419e-a7d3-8f0c733af4c1 | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--d455330d-f190-4854-8087-4c2c37003b45 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--52bfd00c-2e5b-4e43-bba6-f3b46e241d7b | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--c58563a8-d757-4476-8ae2-beb2acce38b3 | 02 October 2023 | 02 October 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--02f547fd-2565-4130-a4be-c4ba7b5aeb0c | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--2452cc82-6ee0-4a98-a213-d5e3f3247e07 | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--39f785a8-4175-4d3c-ba64-e20ad4bc2584 | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--d2985b8a-7a29-4b57-b2f1-cddd79fe4242 | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--7be2d11d-87be-4d1c-8f5b-b7e59ad191ea | 28 September 2023 | 28 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--3a20ed21-5e69-4a16-a0e3-bace3eba9974 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--f531e763-3550-40ba-a6a1-81e208ca12c6 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--1736df4d-188e-4a44-a8b3-6c6cd71dc749 | 29 September 2023 | 29 September 2023
T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--011f1d16-c9f1-48ac-94f1-165466c155f8 | 29 September 2023 | 29 September 2023
T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--c5a69738-3e80-421d-aba2-bdab8a4029fd | 29 September 2023 | 29 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--dbcc492c-782e-4418-8373-dbc7a76498b0 | 29 September 2023 | 29 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--c41d20c8-b99e-4de8-a0e5-3e0ef3b4275b | 02 October 2023 | 02 October 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--83a964cb-730c-44e4-859b-b5246159396b | 29 September 2023 | 29 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--159fb736-ba92-4564-aa6d-db6f64497763 | 28 September 2023 | 28 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--3b7f39cb-0101-49b0-ab02-a5adb1672688 | 28 September 2023 | 28 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--7bd46875-7d59-4d65-8f9b-d48d3cb54a84 | 28 September 2023 | 28 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--3731962f-64e7-4750-ac8b-40b97eef8725 | 29 September 2023 | 29 September 2023
T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--e49e0138-4247-4f3e-a42c-f0dab2f6ffbc | 29 September 2023 | 29 September 2023
T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--03aab956-54f3-4e4b-93a7-6d1898d91b57 | 29 September 2023 | 29 September 2023
T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--8ed7e323-578c-4a62-bf32-0bf2fefa872b | 29 September 2023 | 29 September 2023
T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--93c336f2-7e7c-4c79-af16-faae03e66121 | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--cf53ff89-3c31-4f8d-83a1-b74dce4c558d | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--9fa6797f-f2cb-4b93-b8eb-f40936e967f3 | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--3f07067f-0cbc-489c-8722-a33399ebd4f9 | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--6795c92f-848f-488e-9c25-d240f99c9b34 | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c27e676e-1ac0-4ec8-bf9d-f540969c6b6f | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--32438a90-406c-40f7-a5ac-a1ca92cd51d5 | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--399126a9-815d-4c3b-9d5e-f57d698ac742 | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--bbeb2eae-7da2-4477-ad8e-8c67b00c53bc | 28 September 2023 | 28 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--6c31c795-935a-41ad-8db1-d74430f4a553 | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--97f42cef-bc2a-47c5-b408-8e38aab4030e | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--a6e9bbe1-3e59-45c0-987a-b5354d602dc7 | 29 September 2023 | 29 September 2023
T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--21058f32-3d6e-4381-9288-5c2248e84cce | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--910bada1-c923-4009-a9ea-da257072f168 | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--1f393d04-36db-4bae-a2a4-53ff12a1240e | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--7b95b2aa-9561-494f-8e02-d36edc14e38b | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f353e8ec-0766-4fbd-86b7-9ea06b52958b | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--798de2f3-218b-4622-a62c-84e3840d45a6 | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--250212f0-a149-4a14-af83-94f7fcedc021 | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--2e32e0fd-24cf-4a41-b56d-98ada9f1db8a | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--09e9ed5d-bf32-4aee-8441-774e21ffbdb6 | 28 September 2023 | 28 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--b774fcb4-43bf-4ff1-98c6-0a94838eacc2 | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--1ba485c9-951e-4e07-8e69-1d0efc372f6b | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--5c61c8a2-bfff-43fb-8397-bff864413d74 | 29 September 2023 | 29 September 2023
T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--c9fb4adb-8064-426a-838d-c93674fb380b | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--c95850f4-4616-435c-b237-f1985833d40e | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--adb41ca8-7d2a-4025-b673-db44c9e1f16b | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--a4c64fbc-bac4-44b8-ba52-8fcfa3f674e5 | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--88edcf36-a6f2-474f-b9c2-7800b34919a2 | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--1bea0610-432c-4cd7-8e0e-8b7bbd09d738 | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--456ff399-4925-45d4-aa84-d930eae5348e | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--a7a2790e-d5ba-4a46-bde3-c698c6ae52ac | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b69905bd-6865-4092-9543-47bd9ae318ec | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--5a97008b-c23b-4890-ba76-c30cf2a18fba | 28 September 2023 | 28 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--4011b9e8-317f-40b9-bd3c-3fb1e99c6542 | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--692ff921-c74d-40a4-ab31-879aba5f247a | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--e434db5d-f201-4411-825f-4a50e1e78c75 | 29 September 2023 | 29 September 2023
T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--f5c91d82-5f7c-4e40-a85a-4f1909ae5545 | 29 September 2023 | 29 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--2f457bef-1721-4e0f-b236-24e4652a31b4 | 29 September 2023 | 29 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--1d6fa472-a1fe-4657-a60d-c7f1c39b1653 | 29 September 2023 | 29 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f13dac1a-090b-40c6-9093-eb4abe0deba8 | 28 September 2023 | 28 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--ab8bf0a3-0eef-4364-a3f9-f6ab6222afed | 28 September 2023 | 28 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--1a96ad0d-84df-4b6b-ba4c-8559de5ec356 | 29 September 2023 | 29 September 2023
T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--75c27f4e-d1e3-490a-9793-a6fc8e326a48 | 29 September 2023 | 29 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--cc5c77ce-c5a3-4791-b80e-09d35282443a | 29 September 2023 | 29 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--818ce9d0-8fc2-4a34-a062-f0e6995bdf32 | 28 September 2023 | 28 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--03e94c12-cd51-4f39-a33d-c66a31bbf361 | 29 September 2023 | 29 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--0c72593d-fcc6-4023-8771-bed5e243310e | 28 September 2023 | 28 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--1af5c5bb-0d97-4c0a-9174-4dee1ff8b185 | 29 September 2023 | 29 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--4a641966-3cc8-4dd6-aa61-1a96cfff4a05 | 28 September 2023 | 28 September 2023
T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--740082b7-2411-473a-a59d-4d46cf12f8b5 | 29 September 2023 | 29 September 2023
T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--8bfeed6a-a0c6-4f11-81b2-f32225c85ac4 | 02 October 2023 | 02 October 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--79407d1e-8e16-48c1-939c-ad92f91dd988 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--374837a0-6109-4c95-bee6-893b25ac71cf | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--25281488-be20-4d83-89d1-1da7ea836037 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--4b6a964f-af5c-4ec2-a309-c1ae6b929596 | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--21470001-67f2-47cf-af21-784e5024ac1d | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--4d76274d-75bc-4cd0-be6a-3d5d99f73cb7 | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--096c3136-dac9-4729-98c0-c8d870f2bd13 | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--1fd5badc-0e9f-462c-9738-550e7e8d8ae3 | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--7d42ba22-9595-4463-8dda-c0e47a154fed | 28 September 2023 | 28 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0014 | Routers | x-mitre-asset--dcb1d1c1-b195-45bf-b4cf-5b98c5b859a5 | asset |  | relationship--9b0b3c25-d87c-452a-a2f9-241234410eb8 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--6a476f56-2c07-43be-8054-d978ee8eb924 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--ed3ef546-566a-46c7-918e-7bfa10d05991 | 29 September 2023 | 29 September 2023
T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--523777f8-4780-4716-807c-08a67450b916 | 29 September 2023 | 29 September 2023
T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--ef60735b-c64b-465c-9e5f-46a4d3a49fb3 | 28 September 2023 | 28 September 2023
T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--46690df4-ddac-4ed4-8987-8706ae68a0cf | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--007a2c53-fc5c-4750-aff0-defb282e178a | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--12d6fc4f-bf06-4146-a387-4cb86f0f44a4 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--a466d5b4-39f0-48c1-9a19-f006dc4cb0ac | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--095456bc-898b-4c76-a062-ff0ea90aeab4 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--84fd1e14-44a8-4eac-9bfc-67b50ea1acf7 | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--577b53a0-44ff-4cc4-b571-455d61e596c0 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--e75f88e6-1ffb-467b-b488-46e91cb3e1e9 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--897cfc36-4253-4e1e-8825-726dbe9088a2 | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--73093c08-ea39-4956-8bff-55e15f6630cd | 28 September 2023 | 28 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--d9de58a6-58fd-499c-ba7d-588239297179 | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--ed66e087-8877-4146-a16a-44cfd144a3d8 | 29 September 2023 | 29 September 2023
T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--81055366-e78b-40e0-a799-4b536ba03db3 | 29 September 2023 | 29 September 2023
T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--a15d718f-af30-4745-a837-887ba8f48727 | 29 September 2023 | 29 September 2023
T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--67dae594-4239-4756-a0bc-dee75de19e4c | 29 September 2023 | 29 September 2023
T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--f0d4d23c-2c8c-4731-9b81-7c86fed25b5d | 29 September 2023 | 29 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--012fd76f-1a10-4e48-9306-10ffae3f61dd | 29 September 2023 | 29 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--372c2e72-d56a-4501-a3bc-31b6b0c8d0be | 28 September 2023 | 28 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--45aae58e-1d09-49de-b4c2-837c6f1d5d8f | 02 October 2023 | 02 October 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--46798892-d849-43fe-8147-b40cc9da291e | 28 September 2023 | 28 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--11840b30-f0d1-4df5-a960-cdb80749c32a | 29 September 2023 | 29 September 2023
T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--d3266f04-3453-492d-b9ea-6fb9d0ce3999 | 29 September 2023 | 29 September 2023
T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--d96788b4-55dd-48df-bb9b-83b33ca24813 | 28 September 2023 | 28 September 2023
T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--8a765743-9caf-4c8a-9c58-6fe2c1993108 | 29 September 2023 | 29 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--84671396-a556-4a5d-9bb9-cac697277371 | 29 September 2023 | 29 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--19e9b914-3cb9-430c-ae02-f8e93fc2d826 | 28 September 2023 | 28 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--b37844c1-0338-44f6-9116-48fa0f079913 | 29 September 2023 | 29 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--8d7e2aa5-129a-4060-88ae-9fc066af13c7 | 28 September 2023 | 28 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--78881a3d-59ad-4fbb-8bd2-69388a068584 | 29 September 2023 | 29 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--e1269074-37f4-460b-8a2a-cd26892d4f8e | 28 September 2023 | 28 September 2023
T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--3526acc8-8834-4aaa-87a5-51e587360cf5 | 29 September 2023 | 29 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--17fd7ffd-63d9-4e1e-8b19-38095b2d65ab | 29 September 2023 | 29 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--18cdfacf-4eba-4049-b85f-d1cab5106c75 | 29 September 2023 | 29 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--58f5c89c-7ed2-4e14-ac07-6e95da16e2f1 | 28 September 2023 | 28 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--71a2c3f5-7383-4bd8-a830-dc2aae62a977 | 28 September 2023 | 28 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--e98892d6-e036-4140-adbb-2932dba51a19 | 28 September 2023 | 28 September 2023
T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--da144dd2-c949-4a7f-8c8d-0cb27c52196a | 29 September 2023 | 29 September 2023
T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--f65fa052-5ad0-4fc3-b579-ee33d1225659 | 28 September 2023 | 28 September 2023
T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--63f863e5-7c00-4474-8e43-bbe8bfb05cc3 | 29 September 2023 | 29 September 2023
T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--3fe69c6d-6722-44ad-bab7-e34981d68daa | 28 September 2023 | 28 September 2023
T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--cbee31a0-716c-4b10-83f0-aa889bfb4749 | 20 October 2023 | 20 October 2023
T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--e915e12c-3d0c-4f60-b119-9414940abb0b | 28 September 2023 | 28 September 2023
T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--ff021e27-63be-41f4-bc4d-2ce75d8a3ecb | 28 September 2023 | 28 September 2023
T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--a1d2df14-6f44-44ac-99c2-3e3f55f53476 | 29 September 2023 | 29 September 2023
T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--bffad8de-a807-4216-9753-008a87d9d77f | 28 September 2023 | 28 September 2023
T0839 | Module Firmware | attack-pattern--efbf7888-f61b-4572-9c80-7e2965c60707 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--5ff26c96-c610-4669-b44e-d6318205be5a | 29 September 2023 | 29 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--6f950c91-125b-46a0-aa40-239b4de2306a | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--e3b04152-0c90-41ff-a333-c5163fa9714f | 29 September 2023 | 29 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--65d42e15-749b-4f86-86c5-b9f1da1e60c5 | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--3bc61c8f-3d04-40bd-8239-a15913056bb2 | 02 October 2023 | 02 October 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--4f3a843b-18e7-46e8-8285-9102a2fe62e5 | 29 September 2023 | 29 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--37048032-b41d-47d8-9c73-7b706bef24d1 | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--99f84b91-32a1-4ade-8de5-5d2a0359302f | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--62abe387-10a2-414b-881c-060b70db2157 | 28 September 2023 | 28 September 2023
T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--2a451896-81aa-4eed-a444-4d04661adeeb | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--6ad3b5cc-7ba1-4287-8c05-d02385f84f72 | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--3471632d-253d-469e-9e8c-3b291b4ae88a | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--65aa5a0d-926c-4b04-9509-f66a99639877 | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--ecaf20c0-d881-45b4-98f2-a456e07d3643 | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--d02812b2-23c3-4dce-bf94-c6e464e86fab | 02 October 2023 | 02 October 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--6754195a-99cd-4b45-bafd-4a374ae79bbd | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--7ed1ad67-942a-424e-ad81-8b69a4f0c706 | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--3ad966be-8cb2-42e6-b696-ef9e3b512e35 | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--df321d74-25d6-42da-80e8-3c9a291cb471 | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--6c9c1c11-c996-4d2b-bbed-d73ae30efd2e | 28 September 2023 | 28 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--2346cbf5-b3c8-4110-a66c-6194251d4d49 | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--f1edb034-6dc6-4d6c-8f75-e2cd12213704 | 29 September 2023 | 29 September 2023
T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--bd869385-5778-4303-8993-cc6412d12303 | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--ce3aad7e-1e15-40c7-916b-e25a647e9986 | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--cb47a3bb-daec-4aa1-9a92-af2a61bb65cd | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--6f1479d9-dfd4-4baa-abd5-9847781ef9bf | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--b7284360-0d80-45bb-8486-263ae8f8fa63 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--503c5256-b611-437e-a4ef-2ee1fd20ab29 | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--a84dd2f5-d4f4-44c1-ba51-4804f40576e1 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--2fd8a76f-4663-4251-a16d-e1f105a854f9 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b1921480-8499-46a9-8396-2a2d747c5861 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--e1f28ed0-ec35-4792-ae02-a2d003bd3df4 | 28 September 2023 | 28 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--a23aefa6-15f5-481c-ac3d-09b8e4b3003b | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--24d17e8f-0c0f-41d1-aa83-8b69b8d30be5 | 29 September 2023 | 29 September 2023
T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--1cf89a8b-c0f6-4ffb-ae39-36e2a9d3b081 | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--37aeaf27-6bbe-4949-ba77-37649e38f8b2 | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--0d52eea3-394e-492b-944b-9ccb6348329d | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--52e828db-58d0-443e-8d94-54d265d9606e | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--3d3c5d24-be5c-42e8-98ca-3b04382df39a | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--9951eb11-8140-420d-8e2d-56fbe0ff0134 | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--32d15d1a-04ba-4035-907a-e2871425e8d1 | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--d5b532fe-3df9-4f92-a0f0-9c92823cdb6a | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--86a8d6aa-beff-4343-a0b2-dd099202b2dc | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--1a9ca148-a456-4b66-805f-a2bdfc7a947d | 28 September 2023 | 28 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--3dd35c9a-146d-4370-80ac-69fed35d81a1 | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--c233df49-e450-4151-8a0f-1765faf3d75a | 29 September 2023 | 29 September 2023
T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--0ba1db3a-389a-4937-975b-d2dc0142cb4b | 29 September 2023 | 29 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--d89d9778-4695-4c97-bf6d-1d0fbabb41fa | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--b2e8914a-91bc-42df-8b64-22e5365ede6f | 29 September 2023 | 29 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--f5621ad9-c905-42e3-b59b-e0ae7b9051c7 | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--dfb20521-91c2-4f55-b92a-dab959759b78 | 29 September 2023 | 29 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--eadb4ca5-ee99-4169-a926-95b1ff82e960 | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--fdc20415-c9a1-405e-80af-3d297894e8fa | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--6c470aa0-b119-4078-80fc-2b66a4d6eac4 | 28 September 2023 | 28 September 2023
T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--c37f097a-9698-412f-9e96-4d350bcd2790 | 29 September 2023 | 29 September 2023
T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--41dbf626-b968-4b51-9f7d-aaea14d39b4d | 28 September 2023 | 28 September 2023
T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--af802091-fee7-4d15-a845-fb4ee3c26d6d | 29 September 2023 | 29 September 2023
T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--432b2dc0-52ff-488f-a5e9-c1e510fc7a0b | 28 September 2023 | 28 September 2023
T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--524ffb0f-40ae-4c97-a098-d14001fffa31 | 29 September 2023 | 29 September 2023
T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--29c2757d-c5f6-4c8d-bbdd-3629cb14dd81 | 29 September 2023 | 29 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--67ae8423-c401-4c11-93d3-0454c288d934 | 29 September 2023 | 29 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--3aa2691d-d88d-4467-ae3e-242b3bac22ea | 28 September 2023 | 28 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--f05a2592-00f9-4f1f-ba55-395af5444b96 | 29 September 2023 | 29 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--def57041-6bb4-453a-bf04-188b9e97a35d | 28 September 2023 | 28 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--a287bc05-20cb-4476-ba1f-15bfde6e601d | 29 September 2023 | 29 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--eb171086-88e1-4f24-bd7e-c3f8b3c3283b | 28 September 2023 | 28 September 2023
T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--d611b750-95e5-4f73-8f16-38db0a34a2e0 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--84fa50ff-bb84-4ab6-b759-658c57532c42 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--232c7049-7609-46a9-8bbe-38672713f853 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--026ba3e5-ae3b-4a8b-83c0-ea8327cd9e50 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--28e89bca-04a2-462f-9d84-d5dc4d55d98e | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--d8f95008-33c9-4572-9916-023d8de449b1 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--04aad4a8-8b8c-45d9-bb34-508fe4792863 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--dac96d76-b9b8-4278-9f5b-62f4992e2ac8 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--0b2d0517-9943-413e-a6f9-30c6d5ce8c42 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--4f7cc4b9-fe3a-4883-97cc-4d2a44c55be9 | 28 September 2023 | 28 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--bb3938a6-85ec-4f34-8bcd-6051de7e9259 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--53d7a78d-1431-49e8-944c-62c875e58a20 | 29 September 2023 | 29 September 2023
T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--2b7d57d7-3802-4b59-99c6-1e1597fe78d1 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--79c6d710-baf4-411e-a3f5-9cb8d42b7c19 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--cfaead3c-3db5-400f-bd15-dfbc57cf0185 | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--aa7a0f45-e027-4d79-8413-5d807f44c1ba | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--fe265dd7-2c1a-4c75-8aa8-12d0c82c7926 | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--d3d4f469-9847-41ef-a478-5eaf6003d483 | 02 October 2023 | 02 October 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--56896f6b-27fe-4396-bfea-d3c1a7580b18 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--368558ce-e8a6-4375-b54f-47c2ab31e38d | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--3a76a181-8706-4bc4-9c66-7e809fec44ca | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--4c1df272-9c2a-4647-8d05-3c0de1613e12 | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--24e1f6cf-44c3-4a3f-9839-5cd6398cc0fe | 28 September 2023 | 28 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--e79825fb-3bd0-41e7-9bdd-257cd3ab44a2 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--e17c3b74-69d8-47b2-88d4-adcaf418ab74 | 29 September 2023 | 29 September 2023
T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--b6309476-8268-4c47-920b-8a556cd8ae4c | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--a2f0b9ba-2d6e-43a5-adca-3ec42dba5ce9 | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--ed3ce006-cf41-46f6-bd86-054314c130dc | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--cf8a816c-30ee-4147-a48f-d797fb145a04 | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--6f72c60e-2739-40b6-b6a9-66d2a3d1833e | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--0b2a6fc5-3416-4d78-96cb-f6325c91ab91 | 02 October 2023 | 02 October 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--287b247f-8ec3-4d8d-a521-050ac8c791ad | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--d7b07d40-fbdb-41e9-b610-57de10fa41e5 | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--2138f4ee-5111-4469-92bb-1fc82a6822b4 | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--9c23121e-14bb-4382-b54d-2ea02a2815b5 | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--32bcf2cf-3311-4ef1-9bf4-4bfe14832b3b | 28 September 2023 | 28 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--e4bc29f2-87c8-491d-b51b-d6cede7c1972 | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--d58d8b19-90bc-4a7f-840d-076be296ff20 | 29 September 2023 | 29 September 2023
T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--43344cd7-5004-4dac-8b62-8899105fa265 | 29 September 2023 | 29 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--a221bbb3-5f4f-4879-ae1d-37e8d3022039 | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--7efa1a31-da21-4925-aab0-96a012d5b2a7 | 29 September 2023 | 29 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--c65e39eb-f6d1-4e3a-9070-b2fa7ea35b36 | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--4059da6f-b52b-4265-8bf9-3ad6154dbde4 | 29 September 2023 | 29 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--75e6adae-06a7-47e9-878e-74ca73004c3b | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--4981a944-b3ad-4d78-9881-a17d458e3422 | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--0bc90405-24a9-4f84-a1bb-bf953dbca016 | 28 September 2023 | 28 September 2023
T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--f7215c1f-7bd7-41bd-8466-76caac225c7c | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--144f6ce7-d2b2-4a76-85d2-251191a0d2cc | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--77f3a64d-227d-487f-8484-89007e05b59f | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--66d041e2-d9e8-46cc-88ee-8e5c1cec8702 | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--d23fd724-563d-4f49-8bcd-09c653728cd3 | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--be0f7d83-2441-4259-b411-46e0d10566b1 | 02 October 2023 | 02 October 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--b33f2abc-a218-425b-9a90-b75445b7e142 | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--09e0c991-1707-431b-a0fd-fd8215e6d552 | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--758773e3-d23d-44db-b5d3-643cde5b41f1 | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--77566f94-5e26-41c9-892f-2f62b395afe7 | 28 September 2023 | 28 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--49242ea8-4813-49f7-8bd4-9668216cceeb | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--0f5710a7-f015-40b8-ad3d-f281699f2b72 | 29 September 2023 | 29 September 2023
T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--bf9f227c-e306-4257-add1-39c7c2e42040 | 29 September 2023 | 29 September 2023
T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--bf8f90a2-4d3a-436d-87d0-eff060fb2302 | 29 September 2023 | 29 September 2023
T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--e95fe824-4df1-49a2-abf7-5d76fb47ef42 | 28 September 2023 | 28 September 2023
T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--f72a7a30-bab4-445b-b226-d5c3cd1a5846 | 29 September 2023 | 29 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--7ebee5d3-ce7f-436c-8b4a-087363d6b858 | 29 September 2023 | 29 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--bd7509cc-a7e5-4e29-b615-225dfbdd3c4a | 28 September 2023 | 28 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--1b94c927-0445-4ed8-80f1-7b31418f60b5 | 29 September 2023 | 29 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--4d7eecfc-4dd6-470c-a604-4c8239ac2be4 | 28 September 2023 | 28 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--db46e84f-435e-4022-b484-e6d2e253660c | 29 September 2023 | 29 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--3334e647-fd5d-481d-a7f9-66f73911a57a | 28 September 2023 | 28 September 2023
T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--97f863d7-e68a-4cc8-ab3b-a7e9a1cc2319 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--2d0bed1d-342b-44a0-aec8-e6d7c6596fa2 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--7584e57f-1258-4c47-b18d-99019a586e6c | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--ed095993-bc85-431e-9621-437143f16d44 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--5968cbde-b3da-46df-a8bd-a30c2d85363b | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--4768c731-3be9-44b8-a217-dfbececa57d9 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--2f9c25af-d2e2-4793-85bf-6e2696384a50 | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--7b814e39-71fc-4e99-b46f-b24eca6cc780 | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--54a7bc3f-c05f-4fb3-a980-ffc8750a0a56 | 28 September 2023 | 28 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--d80f9deb-ba2a-4a07-aa23-81c423cf4a18 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--59b53303-e4df-49ec-8e5a-812f2b4265a8 | 29 September 2023 | 29 September 2023
T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--605f3853-b007-4134-8a2d-6a81a35e7676 | 29 September 2023 | 29 September 2023
T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--3843dcca-62a2-4224-9241-05f981fa880a | 28 September 2023 | 28 September 2023
T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--0d8e0324-ba8e-4712-a123-60377afe94da | 29 September 2023 | 29 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--3212de2a-6635-4b95-aeb4-9c0744aed2ce | 28 September 2023 | 28 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--69f4ed24-c2f7-49e1-99a2-350cc2795820 | 29 September 2023 | 29 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--dd9abe36-1cee-4100-a94f-105d9678fd1f | 29 September 2023 | 29 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--e6af4cbd-1b2e-4733-be57-43a845f465eb | 28 September 2023 | 28 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b352884f-2a60-41c6-b348-0bbb5859802a | 28 September 2023 | 28 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--f5c9f641-a498-46b5-9068-39502db53cfd | 28 September 2023 | 28 September 2023
T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--bf5356b1-d00e-43c3-ba92-ae504a737d76 | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--7b1e00af-11fb-4862-a193-55dc9b6652c0 | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--5131c799-517c-4bad-ba97-46ad7de956e7 | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--5425d1cd-8840-4640-90a3-72f3bd7151bd | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--ba496af3-2d99-4c2b-8ce0-20388f5d632c | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--9f2926a2-596f-459e-827e-6fe2d4646efd | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--22548926-29b4-4882-9878-633375489c0e | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--39e5a489-f557-4130-a285-e0a82f40685c | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--2ecf9476-b546-44ff-8547-4ca56cf7eeb8 | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--df9f5a5b-0662-4904-8e57-bc25c244a6da | 28 September 2023 | 28 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--b7344dfb-621b-4558-ab22-6c1f256ee746 | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--ebc9f35c-6f95-4bc0-b8b3-f9b515690fa0 | 29 September 2023 | 29 September 2023
T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--7c433b29-0ad3-4574-990f-e3d6291e7f23 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--943a9a5c-7826-451d-ac73-34353ea40595 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--3f92c11b-f6e2-4c07-9913-9fa7469ba4fe | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--208fe57b-cf2e-4188-8a6f-77597cd60351 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--0750563d-a86c-4822-ab9c-0f2d3c304c6e | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--fd3bc308-82cd-49c9-a41e-9b19ce04b3cd | 02 October 2023 | 02 October 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--da771d72-c778-4c9a-acb4-01b5fc3d36c0 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--f08d487a-7837-48f9-9301-fe0f9f144c92 | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--5e324da5-0fee-4dac-b289-410d560e03e9 | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--b411f748-a1e9-40c6-8eb3-72f2de4dab08 | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--19df16da-8247-45ef-be13-ba58b1fb9c1c | 28 September 2023 | 28 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--dead5325-7efe-4dcc-bf78-42b9190f74da | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--c1e051ab-0a11-4d29-b98f-aa442ab69553 | 29 September 2023 | 29 September 2023
T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--d775a6ed-4a60-41f4-ac06-da86c27cd1de | 29 September 2023 | 29 September 2023
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--73c358d5-f4ce-4ce5-aa3d-d2ede8aff148 | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--46e4cdd2-e8f0-46aa-9264-868815a05af9 | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--deb83319-bc5a-4b9b-a44a-bd369b899601 | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--bad056aa-b8a6-4c4c-9bfa-bcc518872341 | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--41a109dd-11d9-4840-a38b-088fc790f45a | 25 March 2024 | 25 March 2024
T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--80cf98bd-b7dc-45cf-91a6-4ab6b79a7f0b | 25 March 2024 | 25 March 2024
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--b4bb8bd7-8984-45de-888f-45c51ab157fa | 29 September 2023 | 29 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--33e33c74-2f17-4bac-bbba-bf4f2a2035e5 | 29 September 2023 | 29 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--beafc44c-228f-4a7e-9d92-ac1b16d730e2 | 28 September 2023 | 28 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--4508bdef-9528-47ae-804c-bc59d1e694e7 | 28 September 2023 | 28 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--817ae105-3ddf-4766-9d26-ca1ec3c64eb6 | 28 September 2023 | 28 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--a45cec05-2d81-4db1-9267-db8be498e0d2 | 29 September 2023 | 29 September 2023
T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--1fd49958-9695-4137-9aaa-57fde4b97cc8 | 29 September 2023 | 29 September 2023
T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--16b74b29-e3b3-49ff-9ff4-cd7ade0f8ff4 | 29 September 2023 | 29 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--af25cacc-6b1a-47d2-8e13-cb2a7e92b379 | 28 September 2023 | 28 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--c4718fa2-2592-44b0-87d0-f866c118a779 | 29 September 2023 | 29 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--f7bdbc1f-d08c-48a0-a474-a79b91526138 | 28 September 2023 | 28 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--22ba5443-ea49-4076-a666-722eb5352f70 | 28 September 2023 | 28 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--9c0db354-c2d6-4db0-bb76-35ae66c01dd1 | 28 September 2023 | 28 September 2023
T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--33bc3e6f-e8cb-40ea-8088-3de39e2490a7 | 29 September 2023 | 29 September 2023
T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--604e1830-11ac-4ccf-a1d0-b22b80c1b024 | 29 September 2023 | 29 September 2023
T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--1c7df4f1-cee5-42c6-a974-29552552666f | 28 September 2023 | 28 September 2023
T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--7bbe6ac7-d0fb-40e4-8537-bdded7173f07 | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0008 | Application Server | x-mitre-asset--973bc51e-c41e-4cec-ac03-9389c71f3d0d | asset |  | relationship--1a900ac4-c150-4b57-a899-990854b01d4b | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0007 | Control Server | x-mitre-asset--ecb81a8b-022e-4529-a404-55cffca7d3a3 | asset |  | relationship--c047df7c-3ed7-455f-8b13-14ced8e93fef | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0009 | Data Gateway | x-mitre-asset--68388d4f-8138-420b-be2b-5a7dfe9ff6b4 | asset |  | relationship--639148fb-d0a5-4a2f-b6a3-a5ceb83d620b | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0006 | Data Historian | x-mitre-asset--e2c3336a-dd93-44d6-8246-f93cf132c499 | asset |  | relationship--d03de729-9235-4ceb-a1c0-935e2088020b | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--1865830b-511d-4302-99f7-6143647a8e40 | 02 October 2023 | 02 October 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0002 | Human-Machine Interface (HMI) | x-mitre-asset--3a95f7e4-4877-4967-b2e8-e287976c3e64 | asset |  | relationship--9e98d88c-4138-4d0e-8db0-cddf956ab500 | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0005 | Intelligent Electronic Device (IED) | x-mitre-asset--75f810ad-b678-4c57-b93b-fdc79bba0c04 | asset |  | relationship--8ccd5f5c-420a-413b-81ef-5e40f401be95 | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0012 | Jump Host | x-mitre-asset--14932ed5-1098-4cc1-9f57-159ab7366787 | asset |  | relationship--15377914-bf08-4c7e-ab00-1e272e2f3c1a | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0003 | Programmable Logic Controller (PLC) | x-mitre-asset--986c455b-0f43-42b6-8360-33ac48bd9990 | asset |  | relationship--6f2ddada-d7df-4788-b5d1-9add185142e0 | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0004 | Remote Terminal Unit (RTU) | x-mitre-asset--1769c499-55e5-462f-bab2-c39b8cd5ae32 | asset |  | relationship--f691dde5-bb2d-411b-a381-b33e0ab673d6 | 28 September 2023 | 28 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0010 | Safety Controller | x-mitre-asset--69d1b1ef-e918-4cfd-9a98-29debd04cb32 | asset |  | relationship--07f11dc3-60d7-42d3-a4f0-82eba85dfe44 | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0011 | Virtual Private Network (VPN) Server | x-mitre-asset--0804f037-a3b9-4715-98e1-9f73d19d6945 | asset |  | relationship--c4a50132-a210-4093-878d-3d6df23ed26e | 29 September 2023 | 29 September 2023
T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--c39be68a-e208-47ac-a7be-6eb6e84d6608 | 29 September 2023 | 29 September 2023
T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--0f5295ce-d705-4541-8dda-c569b126d103 | 02 October 2023 | 02 October 2023
T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--4b853b7c-bc55-4599-b88d-d08d651526c0 | 29 September 2023 | 29 September 2023
T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | targets | A0013 | Field I/O | x-mitre-asset--2b676abd-8263-49ea-81a4-78a7e1f776fe | asset |  | relationship--1429cd78-4e2a-4898-a7d8-d01a0c465bd6 | 02 October 2023 | 02 October 2023
T0887 | Wireless Sniffing | attack-pattern--0fe075d5-beac-4d02-b93e-0f874997db72 | technique | targets | A0001 | Workstation | x-mitre-asset--f1315d02-9118-4e3b-8cdf-4c2d3f77ce41 | asset |  | relationship--bac1f95c-87bf-4939-bc1a-7727aad738f7 | 29 September 2023 | 29 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | S0089 | BlackEnergy | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | software | (Citation: Booz Allen Hamilton) | relationship--c8e78d6f-ac9d-4ad3-ae13-238f1eb4423a | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | (Citation: Booz Allen Hamilton) | relationship--1dad5efc-395f-4b92-8f4f-3e987a4d5e57 | 27 September 2023 | 27 September 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | Within the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Industroyer](https://attack.mitre.org/software/S0604) was used to target and disrupt the Ukrainian power grid substation components.(Citation: Dragos Crashoverride 2018)(Citation: ESET Industroyer) | relationship--57e8711a-9aae-4a22-94d4-f4c8a3a8f141 | 31 March 2023 | 07 April 2023
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | [TEMP.Veles](https://attack.mitre.org/groups/G0088) leveraged [Triton](https://attack.mitre.org/software/S1009) to interact and disrupt Triconex safety instrumented systems throughout this campaign.(Citation: FireEye TEMP.Veles 2018)(Citation: FireEye TRITON 2018)(Citation: FireEye TRITON Dec 2017) | relationship--533bd747-2567-4c53-a10b-938734f8aeab | 25 March 2024 | 10 April 2024
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) blocked command messages by using malicious firmware to render serial-to-ethernet converters inoperable. (Citation: Ukraine15 - EISAC - 201603) | relationship--57510758-786a-4f0a-aab2-101eaf4e7b9f | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) blocked reporting messages by using malicious firmware to render serial-to-ethernet converters inoperable. (Citation: Ukraine15 - EISAC - 201603) | relationship--9fb8c8ab-67de-42df-a82d-b6e45b82d949 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) overwrote the serial-to-ethernet converter firmware, rendering the devices not operational. This meant that communication to the downstream serial devices was either not possible or more difficult. (Citation: Booz Allen Hamilton) | relationship--3fb86696-1d56-42d5-a73d-044a78b588fe | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) used port 443 to communicate with their C2 servers. (Citation: Booz Allen Hamilton) | relationship--6573327e-3757-424e-8570-04ffe7d5d0e2 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) established an internal proxy prior to the installation of backdoors within the network. (Citation: Booz Allen Hamilton) | relationship--13d76624-7049-45c5-94d3-8f172b7f6336 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [KillDisk](https://attack.mitre.org/software/S0607) rendered devices that were necessary for remote recovery unusable, including at least one RTU. Additionally, [Sandworm Team](https://attack.mitre.org/groups/G0034) overwrote the firmware for serial-to-ethernet converters, denying operators control of the downstream devices. (Citation: Booz Allen Hamilton)(Citation: Ukraine15 - EISAC - 201603) | relationship--97756c8a-b702-472b-8d67-15464a73093e | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), power company phone line operators were hit with a denial of service attack so that they couldn’t field customers’ calls about outages. Operators were also denied service to their downstream devices when their serial-to-ethernet converters had their firmware overwritten, which bricked the devices. (Citation: Ukraine15 - EISAC - 201603) | relationship--7d752615-33f0-44ed-a156-25d84f384e75 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) scheduled the uninterruptable power supplies (UPS) to shutdown data and telephone servers via the UPS management interface. (Citation: Ukraine15 - EISAC - 201603)(Citation: Booz Allen Hamilton) | relationship--8b7403f5-90d2-4d2c-a484-87d29f419a9f | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) used Valid Accounts taken from the Windows Domain Controller to access the control system Virtual Private Network (VPN) used by grid operators. (Citation: Booz Allen Hamilton) | relationship--00b9e63b-57a7-408e-83d6-fc03535010a6 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0823 | Graphical User Interface | attack-pattern--b0628bfc-5376-4a38-9182-f324501cb4cf | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) utilized HMI GUIs in the SCADA environment to open breakers. (Citation: Ukraine15 - EISAC - 201603) | relationship--8d0d6365-7bc0-417d-9268-c7c31fcb0d91 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) moved their tools laterally within the ICS network. (Citation: Booz Allen Hamilton) | relationship--8a86ad59-dff1-46dc-8ffd-3c62b96c6e62 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) opened the breakers at the infected sites, shutting the power off for thousands of businesses and households for around 6 hours. (Citation: Ukraine15 - EISAC - 201603)(Citation: Booz Allen Hamilton) | relationship--f7c5bd1b-c596-41b2-b415-2bf5179667df | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), operators were shut out of their equipment either through the denial of peripheral use or the degradation of equipment. Operators were therefore unable to recover from the incident through their traditional means. Much of the power was restored manually. (Citation: Ukraine15 - EISAC - 201603) | relationship--d1388bba-9869-4e3e-a6c9-430784ad924d | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), power breakers were opened which caused the operating companies to be unable to deliver power, and left thousands of businesses and households without power for around 6 hours. (Citation: Ukraine15 - EISAC - 201603)(Citation: Booz Allen Hamilton) | relationship--423271c0-04dc-42d0-8e27-fb0b6067e096 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) opened live breakers via remote commands to the HMI, causing blackouts. (Citation: Ukraine15 - EISAC - 201603) | relationship--4f83cc15-274d-44c6-859f-e598e362e76e | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) used an IT helpdesk software to move the mouse on ICS control devices to maliciously release electricity breakers. (Citation: Andy Greenberg June 2017) | relationship--352ed52c-88ba-4731-a917-4c33da0f29d4 | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) remotely discovered operational assets once on the OT network. (Citation: Charles McLellan March 2016) (Citation: Booz Allen Hamilton) | relationship--a57b233b-6613-4f78-aa48-e85518aaa7cf | 27 September 2023 | 27 September 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) overwrote the serial-to-ethernet gateways with custom firmware to make systems either disabled, shutdown, and/or unrecoverable. (Citation: Ukraine15 - EISAC - 201603) | relationship--24885921-734f-46c1-85d7-3f79e0b886d6 | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) issued unauthorized commands to substation breaks after gaining control of operator workstations and accessing a distribution management system (DMS) application. (Citation: Ukraine15 - EISAC - 201603) | relationship--acace658-da7e-4a19-aa98-8aec8c966dde | 27 September 2023 | 04 October 2023
C0028 | 2015 Ukraine Electric Power Attack | campaign--46421788-b6e1-4256-b351-f8beffd1afba | campaign | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | During the [2015 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0028), [Sandworm Team](https://attack.mitre.org/groups/G0034) used valid accounts to laterally move through VPN connections and dual-homed systems. Sandworm Team used the credentials of valid accounts to interact with client applications and access employee workstations hosting HMI applications. (Citation: Ukraine15 - EISAC - 201603)(Citation: Booz Allen Hamilton) | relationship--2f0d1a71-7cb6-4979-b072-a859d117d47f | 27 September 2023 | 04 October 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) supplied the name of the payload DLL to [Industroyer](https://attack.mitre.org/software/S0604) via a command line parameter.(Citation: ESET Industroyer) | relationship--b07e6896-a840-49a1-8d58-94396a902b95 | 31 March 2023 | 31 March 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) used a VBS script to facilitate lateral tool transfer. The VBS script was used to copy ICS-specific payloads with the following command: `cscript C:\Backinfo\ufn.vbs C:\Backinfo\101.dll C:\Delta\101.dll`(Citation: Dragos Crashoverride 2018) | relationship--49966e16-04a2-4fd7-86cd-aa934040a9d8 | 31 March 2023 | 07 April 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) transferred executable files as .txt and then renamed them to .exe, likely to avoid detection through extension tracking.(Citation: Dragos Crashoverride 2018) | relationship--e156609f-c30b-4bf5-8a1b-9689ba778a14 | 31 March 2023 | 07 April 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) used MS-SQL access to a pivot machine, allowing code execution throughout the ICS network.(Citation: Dragos Crashoverride 2018) | relationship--4b98b72c-a093-4917-a21b-a0b4f388e98e | 31 March 2023 | 07 April 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) utilized VBS and batch scripts for file movement and as wrappers for PowerShell execution.(Citation: Dragos Crashoverride 2018) | relationship--7bd6e5e4-6614-41ed-8a84-8eb633a91e07 | 31 March 2023 | 07 April 2023
C0025 | 2016 Ukraine Electric Power Attack | campaign--aa73efef-1418-4dbe-b43c-87a498e97234 | campaign | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | During the [2016 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0025), [Sandworm Team](https://attack.mitre.org/groups/G0034) used valid accounts to laterally move through VPN connections and dual-homed systems.(Citation: Dragos Crashoverride 2018) | relationship--a6479493-6154-408f-90df-9d2f3ae352d1 | 31 March 2023 | 07 April 2023
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0895 | Autorun Image | attack-pattern--77d9c726-b53e-481d-8bcc-1068aebfbb9d | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) used existing hypervisor access to map an ISO image named `a.iso` to a virtual machine running a SCADA server. The SCADA server’s operating system was configured to autorun CD-ROM images, and as a result, a malicious VBS script on the ISO image was automatically executed.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--d4da5e90-7986-4c8a-bfb6-df4c0586ce87 | 27 March 2024 | 17 April 2024
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) leveraged the SCIL-API on the MicroSCADA platform to execute commands through the `scilc.exe` binary.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--df88d021-cb8e-482d-9260-445d0a0244ac | 27 March 2024 | 17 April 2024
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) utilizes a Visual Basic script `lun.vbs` to execute `n.bat` which then executed the MicroSCADA `scilc.exe` command.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--43b11545-3b70-4284-a369-bed7a0de4fd0 | 27 March 2024 | 17 April 2024
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0894 | System Binary Proxy Execution | attack-pattern--1c5cf58c-a34a-40d7-82f4-f987cdfc2b91 | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) executed a MicroSCADA application binary `scilc.exe` to send a predefined list of SCADA instructions specified in a file defined by the adversary, `s1.txt`. The executed command `C:\sc\prog\exec\scilc.exe -do pack\scil\s1.txt` leverages the SCADA software to send unauthorized command messages to remote substations.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--984d517f-56a1-4eb4-95e5-994eb9c6c3b5 | 27 March 2024 | 17 April 2024
C0034 | 2022 Ukraine Electric Power Attack | campaign--df8eb785-70f8-4300-b444-277ba849083d | campaign | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | During the [2022 Ukraine Electric Power Attack](https://attack.mitre.org/campaigns/C0034), [Sandworm Team](https://attack.mitre.org/groups/G0034) used the MicroSCADA SCIL-API to specify a set of SCADA instructions, including the sending of unauthorized commands to substation devices.(Citation: Mandiant-Sandworm-Ukraine-2022) | relationship--7cd47eb6-e73a-4a0b-a62e-7e066090b804 | 27 March 2024 | 17 April 2024
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0878 | Alarm Suppression | attack-pattern--2900bbd8-308a-4274-b074-5b8bde8347bc | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary suppressed alarm reporting to the central computer.(Citation: Marshall Abrams July 2008) | relationship--c1154a56-6f5f-4760-8b34-79b0e8a79c1f | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0879 | Damage to Property | attack-pattern--83ebd22f-b401-4d59-8219-2294172cf916 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary gained remote computer access to the control system and altered data so that whatever function should have occurred at affected pumping stations did not occur or occurred in a different way. This ultimately led to 800,000 liters of raw sewage being spilled out into the community. The raw sewage affected local parks, rivers, and even a local hotel. This resulted in harm to marine life and produced a sickening stench from the community's affected rivers.(Citation: Marshall Abrams July 2008) | relationship--642cae89-bb5c-46f3-9fea-8d747b930c35 | 10 March 2023 | 05 April 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary temporarily shut an investigator out of the network preventing them from issuing any controls.(Citation: Marshall Abrams July 2008) | relationship--adf2072c-0341-4fc2-9d25-495b4af864e9 | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary temporarily shut an investigator out of the network, preventing them from viewing the state of the system.(Citation: Marshall Abrams July 2008) | relationship--e0da1f92-82b1-4096-86c4-1aef58ca89fb | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0822 | External Remote Services | attack-pattern--8d2f3bab-507c-4424-b58b-edc977bd215c | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary gained remote computer access to the system over radio.(Citation: Marshall Abrams July 2008) | relationship--245c8c36-28e5-4508-a585-7768cb33299a | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0838 | Modify Alarm Settings | attack-pattern--e5de767e-f513-41cd-aa15-33f6ce5fbf92 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary disabled alarms at four pumping stations, preventing notifications to the central computer.(Citation: Marshall Abrams July 2008) | relationship--268b9429-b1c6-4bc3-84cf-8512e8ef57a7 | 10 March 2023 | 05 April 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary gained remote computer access to the control system and altered data so that whatever function should have occurred at affected pumping stations did not occur or occurred in a different way. The software program installed in the laptop was one developed for changing configurations in the PDS computers. This ultimately led to 800,000 liters of raw sewage being spilled out into the community.(Citation: Marshall Abrams July 2008) | relationship--668f8c4b-225a-4287-ac5b-7717a4f75b5d | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0848 | Rogue Master | attack-pattern--b14395bd-5419-4ef4-9bd8-696936f509bb | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary falsified network addresses in order to send false data and instructions to pumping stations.(Citation: Marshall Abrams July 2008) | relationship--b4efcbe0-ffe3-4d9a-8dba-570e68494af1 | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0856 | Spoof Reporting Message | attack-pattern--8535b71e-3c12-4258-a4ab-40257a1becc4 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary used a dedicated analog two-way radio system to send false data and instructions to pumping stations and the central computer.(Citation: Marshall Abrams July 2008) | relationship--6e329090-fc8c-4a7f-bbf9-08067ad9ebe5 | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0864 | Transient Cyber Asset | attack-pattern--35392fb4-a31d-4c6a-b9f2-1c65b7f5e6b9 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary utilized a computer, possibly stolen, with proprietary engineering software to communicate with a wastewater system.(Citation: Marshall Abrams July 2008) | relationship--59cb471f-ad8b-464f-ab8f-c267f329b0dc | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary used a dedicated analog two-way radio system to send false data and instructions to pumping stations and the central computer.(Citation: Marshall Abrams July 2008) | relationship--c2484b15-7dd0-4280-8898-a6a7da6f0ca2 | 10 March 2023 | 10 March 2023
C0020 | Maroochy Water Breach | campaign--70cab19e-1745-425e-b3db-c02cd5ff157a | campaign | uses | T0860 | Wireless Compromise | attack-pattern--2877063e-1851-48d2-bcc6-bc1d2733157e | technique | In the [Maroochy Water Breach](https://attack.mitre.org/campaigns/C0020), the adversary used a two-way radio to communicate with and set the frequencies of Maroochy Shire's repeater stations.(Citation: Marshall Abrams July 2008) | relationship--ae7ed6d8-65cc-45a0-82c3-c28e5630bf7c | 10 March 2023 | 10 March 2023
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) changed phone numbers tied to certain specific accounts in a designated contact list. They then used the changed phone numbers to redirect network traffic to websites controlled by them, thereby allowing them to capture and use any login codes sent to the devices via text message.(Citation: Triton-EENews-2017) | relationship--03b4dae7-3b20-4ea9-9f7c-6c97582f98b7 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088)’ tool took one option from the command line, which was a single IP address of the target Triconex device.(Citation: FireEye TRITON Dec 2017) | relationship--3a04717f-b74c-4096-b031-ee7115fdc3c9 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) would programmatically return the controller to a normal running state if the [Triton](https://attack.mitre.org/software/S1009) malware failed. If the controller could not recover in a defined time window, [TEMP.Veles](https://attack.mitre.org/groups/G0088) programmatically overwrote their malicious program with invalid data.(Citation: FireEye TRITON Dec 2017) | relationship--b05d678b-4d87-4261-9366-f8b757a77661 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) made attempts on multiple victim machines to transfer and execute the WMImplant tool.(Citation: FireEye TEMP.Veles 2018) | relationship--c137fcd2-ce51-4e17-9c2f-f1aaf9b64ce7 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) tripped a controller into a failed safe state, which caused an automatic shutdown of the plant, this resulted in a pause of plant operations for more than a week. Thereby impacting industrial processes and halting productivity.(Citation: FireEye TRITON Dec 2017) | relationship--5beda54d-cd1f-491b-a85e-d7618a0683ad | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) downloaded multiple rounds of control logic to the Safety Instrumented System (SIS) controllers through a program append operation.(Citation: FireEye TRITON Dec 2017) | relationship--81352e47-4317-45e3-88b9-a97dd2166727 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) utilized remote desktop protocol (RDP) jump boxes, poorly configured OT firewalls (Citation: Triton-EENews-2017), along with other traditional malware backdoors, to move into the ICS environment.(Citation: FireEye TRITON 2018)(Citation: Triton-EENews-2017) | relationship--cd6f1ca4-aaec-451d-b855-55cdb0c3dde8 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) used a publicly available PowerShell-based tool, WMImplant.(Citation: FireEye TEMP.Veles 2018) | relationship--3db8d8d2-89bb-4241-afeb-9b9332aac78e | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) leveraged [Triton](https://attack.mitre.org/software/S1009) to send unauthorized command messages to the Triconex safety controllers.(Citation: FireEye TRITON 2018) | relationship--fd7247a4-b299-4948-a3b0-9b43f4f41ae0 | 28 March 2024 | 10 April 2024
C0030 | Triton Safety Instrumented System Attack | campaign--45a98f02-852f-49b2-94c0-c63207bebbbf | campaign | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | In the [Triton Safety Instrumented System Attack](https://attack.mitre.org/campaigns/C0030), [TEMP.Veles](https://attack.mitre.org/groups/G0088) used valid credentials when laterally moving through RDP jump boxes into the ICS environment.(Citation: FireEye TRITON 2018) | relationship--bf0e7347-1636-4b5e-9e2a-8b93177e5f85 | 28 March 2024 | 10 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0812 | Default Credentials | attack-pattern--8bb4538f-f16f-49f0-a431-70b5444c7349 | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) discovered and exploited default credentials found on many Unitronics [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002). For many of these devices, the default password was set to ‘1111’.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: CISA Unitronics November 2023) | relationship--1acc3a43-2961-4e4c-a237-f426a2df6be5 | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) defaced controllers’ [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002), which prevented multiple entities from being able to operate their devices normally.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: CISA Unitronics November 2023)(Citation: Jamie Tarabay and Katrina Manson December 2023)(Citation: Frank Bajak and Marc Levy December 2023) Additionally, the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) caused a communications failure in a remote pumping station.(Citation: WPXI Aliquippa Water November 2023) | relationship--18ab56e8-79ce-481d-9ab4-e558fbfb5ac5 | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0883 | Internet Accessible Device | attack-pattern--f8df6b57-14bc-425f-9a91-6f59f6799307 | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) exploited devices connected to the public internet, such as internet connected Unitronics [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) with [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002) and networking equipment such as cellular modems found in OT environments.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: Lisa Zahner December 2023) | relationship--6b0e8f60-ecdf-4140-9741-5b50df67353c | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) caused multiple businesses to halt operations due to the unavailability of the [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) and [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002). These victims covered multiple sectors.(Citation: Jamie Tarabay and Katrina Manson December 2023) | relationship--1673b2e2-7799-4b5f-b5a9-2c51426a6916 | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) caused multiple businesses to halt operations in their industrial environments, impacting their typical business operations. These victims covered multiple sectors.(Citation: Jamie Tarabay and Katrina Manson December 2023) | relationship--d67ae959-9014-4501-b963-42bee03a5e3b | 25 March 2024 | 15 April 2024
C0031 | Unitronics Defacement Campaign | campaign--8fda050f-470d-4401-994e-35c1a6c301de | campaign | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | During the [Unitronics Defacement Campaign](https://attack.mitre.org/campaigns/C0031), the [CyberAv3ngers](https://attack.mitre.org/groups/G1027) replaced the existing graphic on the [Programmable Logic Controller (PLC)](https://attack.mitre.org/assets/A0003) [Human-Machine Interface (HMI)](https://attack.mitre.org/assets/A0002) with their own, thereby preventing PLC owners and operators from viewing PLC information on the HMI.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)(Citation: Jamie Tarabay and Katrina Manson December 2023) | relationship--69889c90-e6d0-4007-9078-2bfbd7c18a91 | 25 March 2024 | 15 April 2024
G0082 | APT38 | intrusion-set--00f67a77-86a4-4adf-be26-1a54fc713340 | group | uses | S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | (Citation: ESET Lazarus KillDisk April 2018) | relationship--cb1037c1-4b83-4a79-ba12-00558bb6b42b | 04 October 2021 | 04 October 2021
G0035 | Dragonfly | intrusion-set--1c63d4ec-0a75-4daa-b1df-0d11af3d3cc1 | group | uses | S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | (Citation: Symantec Dragonfly)(Citation: Gigamon Berserk Bear October 2021) | relationship--d4968f45-d06b-4843-8f72-6e08beb94cab | 31 May 2017 | 07 December 2021
G0037 | FIN6 | intrusion-set--2a7914cf-dff3-428d-ab0f-1014d1c28aeb | group | uses | S0372 | LockerGoga | malware--5af7a825-2d9f-400d-931a-e00eb9e27f48 | software | (Citation: FireEye FIN6 Apr 2019) | relationship--ad7770c3-fe24-4285-9ce2-1616a1061472 | 17 April 2019 | 28 June 2019
G0037 | FIN6 | intrusion-set--2a7914cf-dff3-428d-ab0f-1014d1c28aeb | group | uses | S0446 | Ryuk | malware--a020a61c-423f-4195-8c46-ba1d21abba37 | software | (Citation: FireEye FIN6 Apr 2019) | relationship--e9f5096e-b9fc-459a-a303-88763b1269cc | 14 May 2020 | 15 May 2020
G0046 | FIN7 | intrusion-set--3753cc21-2dae-4dfb-8481-d004e74502cc | group | uses | S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | (Citation: IBM Ransomware Trends September 2020)(Citation: CrowdStrike Carbon Spider August 2021)(Citation: FBI Flash FIN7 USB)(Citation: Microsoft Ransomware as a Service) | relationship--65adbdda-7069-40ed-9825-b79ec87e4916 | 21 September 2021 | 04 December 2023
G0115 | GOLD SOUTHFIELD | intrusion-set--c77c5576-ca19-42ed-a36f-4b4486a84133 | group | uses | S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | (Citation: Secureworks REvil September 2019)(Citation: Secureworks GandCrab and REvil September 2019) | relationship--bff99f91-e1a9-4379-a2d9-5a99615a95d1 | 22 September 2020 | 22 September 2020
G0032 | Lazarus Group | intrusion-set--c93fccb1-e8e8-42cf-ae33-2ad1d183913a | group | uses | S0366 | WannaCry | malware--75ecdbf1-c2bb-4afc-a3f9-c8da4de8c661 | software | (Citation: FireEye APT38 Oct 2018)(Citation: LogRhythm WannaCry)(Citation: FireEye WannaCry 2017)(Citation: SecureWorks WannaCry Analysis) | relationship--25e7ca82-2784-433a-90a9-a3483615a655 | 12 April 2019 | 09 September 2019
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | (Citation: Secureworks IRON VIKING ) | relationship--129a4d3f-fa4a-42c3-833e-8f15155b9693 | 09 March 2022 | 09 March 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | S0089 | BlackEnergy | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | software | (Citation: iSIGHT Sandworm 2014)(Citation: F-Secure BlackEnergy 2014)(Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: UK NCSC Olympic Attacks October 2020)(Citation: Secureworks IRON VIKING ) | relationship--b349ef5f-4a05-4eef-afe4-1543b8c832fa | 31 May 2017 | 28 February 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | (Citation: Dragos Crashoverride 2018)(Citation: Dragos Crashoverride 2017)(Citation: ESET Industroyer)(Citation: Secureworks IRON VIKING) | relationship--9f07c92a-78a0-438a-8cb2-01e2bddaeb42 | 04 January 2021 | 12 October 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | (Citation: Industroyer2 ESET April 2022) | relationship--9f43126d-5f6c-42a9-9908-49175c27ead7 | 30 March 2023 | 05 April 2023
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | (Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: Secureworks IRON VIKING ) | relationship--ce64ed04-f0ff-4897-b636-3177c9c5d9bb | 20 January 2021 | 28 February 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | S0368 | NotPetya | malware--5719af9d-6b16-46f9-9b28-fb019541ddbb | software | (Citation: NCSC Sandworm Feb 2020)(Citation: US District Court Indictment GRU Unit 74455 October 2020)(Citation: UK NCSC Olympic Attacks October 2020)(Citation: Secureworks IRON VIKING )(Citation: Trend Micro Cyclops Blink March 2022) | relationship--c5dd0d66-99f1-4efd-b0f9-bf9f9118ff16 | 10 June 2020 | 17 March 2022
G0088 | TEMP.Veles | intrusion-set--9538b1a4-4120-4e2d-bf59-3b11fcab05a4 | group | uses | S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | (Citation: Dragos Xenotime 2018) | relationship--9b825e77-2b18-4bc8-8e1d-5f645d570dca | 17 October 2018 | 23 November 2022
G0102 | Wizard Spider | intrusion-set--dd2d9ca6-505b-4860-a604-233685b802c7 | group | uses | S0446 | Ryuk | malware--a020a61c-423f-4195-8c46-ba1d21abba37 | software | (Citation: CrowdStrike Ryuk January 2019)(Citation: Red Canary Hospital Thwarted Ryuk October 2020)(Citation: DHS/CISA Ransomware Targeting Healthcare October 2020)(Citation: FireEye KEGTAP SINGLEMALT October 2020)(Citation: DFIR Ryuk's Return October 2020)(Citation: DFIR Ryuk 2 Hour Speed Run November 2020)(Citation: DFIR Ryuk in 5 Hours October 2020)(Citation: Sophos New Ryuk Attack October 2020)(Citation: CrowdStrike Wizard Spider October 2020)(Citation: Mandiant FIN12 Oct 2021)(Citation: Microsoft Ransomware as a Service) | relationship--6895e54e-3968-41a9-9013-a082cd46fa44 | 14 May 2020 | 04 December 2023
G1000 | ALLANITE | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | group | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [ALLANITE](https://attack.mitre.org/groups/G1000) leverages watering hole attacks to gain access into electric utilities. (Citation: Eduard Kovacs May 2018) | relationship--fc4803cb-d6bf-4674-bf40-d4b0997824ba | 18 April 2018 | 12 October 2022
G1000 | ALLANITE | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | group | uses | T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | [ALLANITE](https://attack.mitre.org/groups/G1000) has been identified to collect and distribute screenshots of ICS systems such as HMIs. (Citation: Dragos) (Citation: ICS-CERT October 2017) | relationship--5424e327-396f-4b07-94a3-408ffc915686 | 18 April 2018 | 12 October 2022
G1000 | ALLANITE | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | group | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [ALLANITE](https://attack.mitre.org/groups/G1000) utilized spear phishing to gain access into energy sector environments. (Citation: Jeff Jones May 2018) | relationship--679e7b8d-57d7-4c1d-8f42-1496606ea666 | 18 April 2018 | 12 October 2022
G1000 | ALLANITE | intrusion-set--190242d7-73fc-4738-af68-20162f7a5aae | group | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | [ALLANITE](https://attack.mitre.org/groups/G1000) utilized credentials collected through phishing and watering hole attacks. (Citation: Dragos) | relationship--0eb112f6-c1cb-4843-93f5-f668aa0e9bd8 | 18 April 2018 | 12 October 2022
G0064 | APT33 | intrusion-set--fbd29c89-18ba-4c2d-b792-51c0adee049f | group | uses | T0852 | Screen Capture | attack-pattern--c5e3cdbc-0387-4be9-8f83-ff5c0865f377 | technique | [APT33](https://attack.mitre.org/groups/G0064) utilize backdoors capable of capturing screenshots once installed on a system. (Citation: Jacqueline O'Leary et al. September 2017)(Citation: Junnosuke Yagi March 2017) | relationship--0beb0088-3bea-4612-b2d9-ff9988f829ae | 18 April 2018 | 12 October 2022
G0064 | APT33 | intrusion-set--fbd29c89-18ba-4c2d-b792-51c0adee049f | group | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | [APT33](https://attack.mitre.org/groups/G0064) utilized PowerShell scripts to establish command and control and install files for execution. (Citation: Symantec March 2019) (Citation: Dragos) | relationship--739e7b8d-57d7-4c1d-8f42-1496606ea666 | 18 April 2018 | 12 October 2022
G0064 | APT33 | intrusion-set--fbd29c89-18ba-4c2d-b792-51c0adee049f | group | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [APT33](https://attack.mitre.org/groups/G0064) sent spear phishing emails containing links to HTML application files, which were embedded with malicious code. (Citation: Jacqueline O'Leary et al. September 2017) [APT33](https://attack.mitre.org/groups/G0064) has conducted targeted spear phishing campaigns against U.S. government agencies and private sector companies. (Citation: Andy Greenburg June 2019) | relationship--0f18b876-b698-4f70-aa98-50e8b5a7eae2 | 18 April 2018 | 12 October 2022
G0035 | Dragonfly | intrusion-set--1c63d4ec-0a75-4daa-b1df-0d11af3d3cc1 | group | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [Dragonfly](https://attack.mitre.org/groups/G0035) utilized watering hole attacks on energy sector websites by injecting a redirect iframe to deliver [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) or [Trojan.Karagany](https://attack.mitre.org/software/S0094). (Citation: Symantec Security Response July 2014) | relationship--042243fd-bfe0-4961-96de-a36232d3ff74 | 18 April 2018 | 12 October 2022
G0035 | Dragonfly | intrusion-set--1c63d4ec-0a75-4daa-b1df-0d11af3d3cc1 | group | uses | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | [Dragonfly](https://attack.mitre.org/groups/G0035) trojanized legitimate ICS equipment providers software packages available for download on their websites.(Citation: Symantec Security Response July 2014) | relationship--ef615d62-fe85-4740-9c5d-5dddff9b5693 | 18 April 2018 | 12 October 2022
G0032 | Lazarus Group | intrusion-set--c93fccb1-e8e8-42cf-ae33-2ad1d183913a | group | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [Lazarus Group](https://attack.mitre.org/groups/G0032) has been observed targeting organizations using spearphishing documents with embedded malicious payloads. (Citation: Novetta Threat Research Group February 2016) Highly targeted spear phishing campaigns have been conducted against a U.S. electric grid company. (Citation: Eduard Kovacs March 2018) | relationship--31bf1721-78a2-4b6c-b325-5c44dc02ea33 | 14 December 2017 | 12 October 2022
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [OilRig](https://attack.mitre.org/groups/G0049) has been seen utilizing watering hole attacks to collect credentials which could be used to gain access into ICS networks. (Citation: Eduard Kovacs May 2018) | relationship--f8318ac4-8ed0-478d-be87-faa2c9d8a740 | 17 October 2018 | 12 October 2022
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | [OilRig](https://attack.mitre.org/groups/G0049) has embedded a macro within spearphishing attachments that has been made up of both a VBScript and a PowerShell script.(Citation: Robert Falcone, Bryan Lee May 2016) | relationship--c4e8dd42-9855-4a36-b915-dc7e1a91e235 | 17 October 2018 | 12 October 2022
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [OilRig](https://attack.mitre.org/groups/G0049) used spearphishing emails with malicious Microsoft Excel spreadsheet attachments. (Citation: Robert Falcone, Bryan Lee May 2016) | relationship--3618a010-b94b-4974-b1be-7630d5c853c1 | 17 October 2018 | 12 October 2022
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [OilRig](https://attack.mitre.org/groups/G0049) communicated with its command and control using HTTP requests. (Citation: Robert Falcone, Bryan Lee May 2016) | relationship--d2dc57eb-5be2-4f9c-a4f7-18d2085ff412 | 17 October 2018 | 12 October 2022
G0049 | OilRig | intrusion-set--4ca1929c-7d64-4aab-b849-badbfc0c760d | group | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | [OilRig](https://attack.mitre.org/groups/G0049) utilized stolen credentials to gain access to victim machines.(Citation: Dragos) | relationship--f65a8ce8-90fa-4d92-a0dc-3ee544c541fe | 17 October 2018 | 12 October 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | [Sandworm Team](https://attack.mitre.org/groups/G0034) uses the MS-SQL server xp_cmdshell command, and PowerShell to execute commands. (Citation: Dragos October 2018) | relationship--26d68f5d-6ee5-4d98-b175-943366ccc038 | 14 October 2020 | 12 October 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | [Sandworm Team](https://attack.mitre.org/groups/G0034) establishes an internal proxy prior to the installation of backdoors within the network. (Citation: Dragos Inc. June 2017) | relationship--eb1e05ef-58df-4c6d-acd7-5cc63ff7f44f | 08 October 2021 | 12 October 2022
G0034 | Sandworm Team | intrusion-set--381fcf73-60f6-4ab2-9991-6af3cbc35192 | group | uses | T0819 | Exploit Public-Facing Application | attack-pattern--32632a95-6856-47b9-9ab7-fea5cd7dce00 | technique | [Sandworm Team](https://attack.mitre.org/groups/G0034) actors exploited vulnerabilities in GE's Cimplicity HMI and Advantech/Broadwin WebAccess HMI software which had been directly exposed to the internet. (Citation: ICS-CERT December 2014) (Citation: ICS CERT September 2018) | relationship--a846dbe5-9ef3-4fb6-93d5-f764671a75c8 | 11 April 2021 | 12 October 2022
G0088 | TEMP.Veles | intrusion-set--9538b1a4-4120-4e2d-bf59-3b11fcab05a4 | group | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [TEMP.Veles](https://attack.mitre.org/groups/G0088) utilizes watering hole websites to target industrial employees. (Citation: Chris Bing May 2018) | relationship--b3862aa6-7bd0-46a4-83b6-bb687bb7caa6 | 17 October 2018 | 12 October 2022
G0088 | TEMP.Veles | intrusion-set--9538b1a4-4120-4e2d-bf59-3b11fcab05a4 | group | uses | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | [TEMP.Veles](https://attack.mitre.org/groups/G0088) targeted several ICS vendors and manufacturers. (Citation: Dragos Threat Intelligence August 2019) | relationship--b343e131-e448-46c6-815b-b86e4bd6d638 | 17 October 2018 | 12 October 2022
S1000 | ACAD/Medre.A | malware--a4a98eab-b691-45d9-8c48-869ef8fefd57 | software | uses | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | [ACAD/Medre.A](https://attack.mitre.org/software/S1000) collects information related to the AutoCAD application. The worm collects AutoCAD (*.dwg) files with drawings from infected systems. (Citation: ESET) | relationship--274994e7-1fe9-463a-9979-46c72107bf9b | 30 March 2023 | 30 March 2023
S1000 | ACAD/Medre.A | malware--a4a98eab-b691-45d9-8c48-869ef8fefd57 | software | uses | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | [ACAD/Medre.A](https://attack.mitre.org/software/S1000) can collect AutoCad files with drawings. These drawings may contain operational information. (Citation: ESET) | relationship--228b9a13-0545-4ecf-99ff-be02addaf7fe | 17 October 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | Using OPC, a component of [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) gathers any details about connected devices and sends them back to the C2 for the attackers to analyze. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--8f76d408-be8a-478e-8a5a-aab1d1f96572 | 18 April 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) payload has caused multiple common OPC platforms to intermittently crash. This could cause a denial of service effect on applications reliant on OPC communications. (Citation: ICS-CERT August 2018) | relationship--d90aeeb6-3686-483a-8403-6514ecfe1a50 | 18 April 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) payload has the capability of enumerating OPC tags, in addition to more generic OPC server information. The server data and tag names can provide information about the names and function of control devices. (Citation: ICS-CERT August 2018) (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--90d9c8e3-0250-4096-8d98-7ca1d324d654 | 12 April 2021 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) ICS malware plugin relies on Windows networking (WNet) to discover all the servers, including OPC servers, that are reachable by the compromised machine over the network. (Citation: Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell December 2015) | relationship--3f76d408-be8a-478e-8a5a-aab1d1f96572 | 18 April 2018 | 11 August 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) payload gathers server information that includes CLSID, server name, Program ID, OPC version, vendor information, running state, group count, and server bandwidth. This information helps indicate the role the server has in the control process. (Citation: ICS-CERT August 2018) (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--067932c3-0011-4ca2-9bbe-721c631e4e41 | 13 April 2021 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) RAT is distributed through a trojanized installer attached to emails. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--e0aee02c-b424-4781-be10-793d71594c31 | 18 April 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0862 | Supply Chain Compromise | attack-pattern--5e0f75da-e108-4688-a6de-a4f07cc2cbe3 | technique | The [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) RAT is distributed through trojanized installers planted on compromised vendor sites. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) | relationship--6d822f86-5793-403a-b176-5d533f6b81b3 | 18 April 2018 | 12 October 2022
S0093 | Backdoor.Oldrea | malware--083bb47b-02c8-4423-81a2-f9ef58572974 | software | uses | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | Execution of [Backdoor.Oldrea](https://attack.mitre.org/software/S0093) relies on a user opening a trojanized installer attached to an email. (Citation: Daavid Hentunen, Antti Tikkanen June 2014) (Citation: Kyle Wilhoit) | relationship--5bb313a8-8407-4ec1-a4b0-683ded7f3302 | 18 April 2018 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0817 | Drive-by Compromise | attack-pattern--7830cfcf-b268-4ac0-a69e-73c6affbae9a | technique | [Bad Rabbit](https://attack.mitre.org/software/S0606) ransomware spreads through drive-by attacks where insecure websites are compromised. While the target is visiting a legitimate website, a malware dropper is being downloaded from the threat actors infrastructure. (Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017) | relationship--0c1fe5fc-3bdc-4d0e-94a0-6564f2ce4444 | 31 May 2017 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | [Bad Rabbit](https://attack.mitre.org/software/S0606) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks. (Citation: Joe Slowik April 2019) | relationship--058396ca-3af4-444b-b261-74485c47e68c | 31 May 2017 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [Bad Rabbit](https://attack.mitre.org/software/S0606) can move laterally through industrial networks by means of the SMB service. (Citation: Joe Slowik April 2019) | relationship--ffc5bbce-8d9c-4276-9dc6-efed5c01af8b | 31 May 2017 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | Several transportation organizations in Ukraine have suffered from being infected by [Bad Rabbit](https://attack.mitre.org/software/S0606), resulting in some computers becoming encrypted, according to media reports. (Citation: Marc-Etienne M.Lveill October 2017) | relationship--d7ea83fa-87c7-4d36-96d5-aee554504040 | 31 May 2017 | 12 October 2022
S0606 | Bad Rabbit | malware--2eaa5319-5e1e-4dd7-bbc4-566fced3964a | software | uses | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | [Bad Rabbit](https://attack.mitre.org/software/S0606) is disguised as an Adobe Flash installer. When the file is opened it starts locking the infected computer. (Citation: Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017) | relationship--edf73653-b2d7-422f-b433-b6a428ff12d4 | 31 May 2017 | 12 October 2022
S0089 | BlackEnergy | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | software | uses | T0865 | Spearphishing Attachment | attack-pattern--648f995e-9c3a-41e4-aeee-98bb41037426 | technique | [BlackEnergy](https://attack.mitre.org/software/S0089) targeted energy sector organizations in a wide reaching email spearphishing campaign. Adversaries utilized malicious Microsoft Word documents attachments. (Citation: Booz Allen Hamilton) | relationship--d9165ecb-bc10-4189-a7e4-057bdf05bf3f | 14 December 2017 | 12 October 2022
S0089 | BlackEnergy | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [BlackEnergy](https://attack.mitre.org/software/S0089) uses HTTP POST request to contact external command and control servers. (Citation: Booz Allen Hamilton) | relationship--3a7d1db3-9383-4171-8938-382e9b0375c6 | 14 December 2017 | 12 October 2022
S0089 | BlackEnergy | malware--54cc1d4f-5c53-4f0e-9ef5-11b4998e82e4 | software | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | [BlackEnergy](https://attack.mitre.org/software/S0089) utilizes valid user and administrator credentials, in addition to creating new administrator accounts to maintain presence. (Citation: Booz Allen Hamilton) | relationship--ee2fdebd-1587-4e53-a7d7-c15fcc88879d | 14 December 2017 | 12 October 2022
S0608 | Conficker | malware--58eddbaf-7416-419a-ad7b-e65b9d4c3b55 | software | uses | T0826 | Loss of Availability | attack-pattern--b5b9bacb-97f2-4249-b804-47fd44de1f95 | technique | A [Conficker](https://attack.mitre.org/software/S0608) infection at a nuclear power plant forced the facility to temporarily shutdown. (Citation: Catalin Cimpanu April 2016) | relationship--990f944f-190d-456d-b194-f5ecb17a0868 | 24 June 2019 | 12 October 2022
S0608 | Conficker | malware--58eddbaf-7416-419a-ad7b-e65b9d4c3b55 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | A [Conficker](https://attack.mitre.org/software/S0608) infection at a nuclear power plant forced the facility to shutdown and go through security procedures involved with such events, with its staff scanning computer systems and going through all the regular checks and motions before putting the plant back into production. (Citation: Catalin Cimpanu April 2016) | relationship--51f9963c-c041-4bec-b482-5fda2fb5bca4 | 24 June 2019 | 12 October 2022
S0608 | Conficker | malware--58eddbaf-7416-419a-ad7b-e65b9d4c3b55 | software | uses | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | [Conficker](https://attack.mitre.org/software/S0608) exploits Windows drive shares. Once it has infected a computer, [Conficker](https://attack.mitre.org/software/S0608) automatically copies itself to all visible open drive shares on other computers inside the network. (Citation: Symantec June 2015) Nuclear power plant officials suspect someone brought in [Conficker](https://attack.mitre.org/software/S0608) by accident on a USB thumb drive, either from home or computers found in the power plant's facility. (Citation: Catalin Cimpanu April 2016) | relationship--71422483-33e4-4131-a4ec-40322d91d8a0 | 24 June 2019 | 17 October 2022
S0038 | Duqu | malware--68dca94f-c11d-421e-9287-7c501108e18c | software | uses | T0811 | Data from Information Repositories | attack-pattern--3405891b-16aa-4bd7-bd7c-733501f9b20f | technique | [Duqu](https://attack.mitre.org/software/S0038) downloads additional modules for the collection of data in information repositories, including the Infostealer 2 module that can access data from Windows Shares.(Citation: Symantec) | relationship--692324b4-064a-430c-8ffc-7f7acd537778 | 17 October 2018 | 30 March 2023
S0038 | Duqu | malware--68dca94f-c11d-421e-9287-7c501108e18c | software | uses | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | [Duqu](https://attack.mitre.org/software/S0038) downloads additional modules for the collection of data from local systems. The modules are named: infostealer 1, infostealer 2 and reconnaissance. (Citation: Symantec) | relationship--172e0537-7a9c-4610-9b07-32a841f0bd8d | 30 March 2023 | 30 March 2023
S0038 | Duqu | malware--68dca94f-c11d-421e-9287-7c501108e18c | software | uses | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | [Duqu](https://attack.mitre.org/software/S0038)'s purpose is to gather intelligence data and assets from entities such as industrial infrastructure and system manufacturers, amongst others not in the industrial sector, in order to more easily conduct a future attack against another third party.(Citation: Symantec) | relationship--792324b4-064a-430c-8ffc-7f7acd537778 | 17 October 2018 | 12 October 2022
S0605 | EKANS | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | [EKANS](https://attack.mitre.org/software/S0605) infection resulted in a temporary production loss within a Honda manufacturing plant. (Citation: Davey Winder June 2020) | relationship--a6519c11-e9d4-4b6f-8d92-8efaa2144c28 | 13 April 2021 | 12 October 2022
S0605 | EKANS | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | software | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | [EKANS](https://attack.mitre.org/software/S0605) masquerades itself as a valid executable with the filename update.exe. Many valid programs use the process name update.exe to perform background software updates. (Citation: Dragos Threat Intelligence February 2020) | relationship--c347b69c-e3f6-4eca-ba57-0781c7dc8eac | 13 April 2021 | 12 October 2022
S0605 | EKANS | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | software | uses | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | [EKANS](https://attack.mitre.org/software/S0605) performs a DNS lookup of an internal domain name associated with its target network to identify if it was deployed on the intended system. (Citation: Ben Hunter and Fred Gutierrez July 2020) | relationship--1dc35f79-0ada-4342-bd13-10d10c1b0335 | 13 April 2021 | 12 October 2022
S0605 | EKANS | malware--00e7d565-9883-4ee5-b642-8fd17fd6a3f5 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | Before encrypting the process, [EKANS](https://attack.mitre.org/software/S0605) first kills the process if its name matches one of the processes defined on the kill-list. (Citation: Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020) (Citation: Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020) EKANS also utilizes netsh commands to implement firewall rules that blocks any remote communication with the device. (Citation: Ben Hunter and Fred Gutierrez July 2020) | relationship--11e4eb54-b0b3-4f67-a93f-28cc10df00ab | 13 April 2021 | 12 October 2022
S0143 | Flame | malware--ff6840c9-4c87-4d07-bbb6-9f50aa33d498 | software | uses | T0893 | Data from Local System | attack-pattern--fa3aa267-da22-4bdd-961f-03223322a8d5 | technique | [Flame](https://attack.mitre.org/software/S0143) has built-in modules to gather information from compromised computers. (Citation: Kevin Savage and Branko Spasojevic) | relationship--25ddb2e0-b945-45d2-a8a9-6e6d5c4401d3 | 30 March 2023 | 30 March 2023
S0143 | Flame | malware--ff6840c9-4c87-4d07-bbb6-9f50aa33d498 | software | uses | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | [Flame](https://attack.mitre.org/software/S0143) can collect AutoCAD design data and visio diagrams as well as other documents that may contain operational information. (Citation: Kevin Savage and Branko Spasojevic) | relationship--79d05cb2-ded0-4847-b52e-af7af421f303 | 14 December 2017 | 12 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can establish a remote HTTP connection to change the operating mode of Omron PLCs.(Citation: Dragos-Pipedream)(Citation: Wylie-22) | relationship--51eb15a3-48af-470f-94c0-10f25b366d72 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | The [INCONTROLLER](https://attack.mitre.org/software/S1045) PLCProxy module can add an IP route to the CODESYS gateway running on Schneider PLCs to allow it to route messages through the PLC to other devices on that network. This allows the malware to bypass firewall rules that prevent it from directly communicating with devices on the same network as the PLC.(Citation: Wylie-22) | relationship--40479f3e-d4d2-45f8-893f-f8a4fcf1613c | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can wipe the memory of Omron PLCs and reset settings through the remote HTTP service.(Citation: Brubaker-Incontroller)(Citation: Dragos-Pipedream)(Citation: Wylie-22) | relationship--e3923fcf-5580-4c1e-bc55-33f67792cc00 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) has the ability to exploit a vulnerable Asrock driver (AsrDrv103.sys) using CVE-2020-15368 to load its own unsigned driver on the system.(Citation: Wylie-22) | relationship--cba8313b-c338-45f7-88ef-a514094882ac | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can login to Omron PLCs using hardcoded credentials, which is documented in CVE-2022-34151.(Citation: Wylie-22) | relationship--1f785984-791e-4612-be32-9ee6903a9c0b | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use a Telnet session to load a malware implant on Omron PLCs.(Citation: CISA-AA22-103A)(Citation: Wylie-22) | relationship--868db512-b897-4a54-ae56-ac78f6c93a14 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the HTTP CGI scripts on Omron PLCs to modify parameters on EtherCat connected servo drives.(Citation: Wylie-22) | relationship--4dd93fd2-6e6d-4c50-a091-6d6ea6903f1e | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can deploy Tcpdump to sniff network traffic and collect PCAP files.(Citation: Wylie-22) | relationship--d8911566-f622-4a01-b765-514dbbfd8201 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0861 | Point & Tag Identification | attack-pattern--25852363-5968-4673-b81d-341d5ed90bd1 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can remotely read the OCP UA structure from devices.(Citation: CISA-AA22-103A) | relationship--064dfd6f-db5d-48e8-b350-9dd47a270911 | 28 September 2022 | 12 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the CODESYS protocol to download programs to Schneider PLCs.(Citation: Wylie-22)(Citation: Brubaker-Incontroller) [INCONTROLLER](https://attack.mitre.org/software/S1045) can modified program logic on Omron PLCs using either the program download or backup transfer functions available through the HTTP server.(Citation: Wylie-22) | relationship--7c1eee62-3307-4e25-8a20-919ccd56ec1c | 29 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the CODESYS protocol to upload programs from Schneider PLCs.(Citation: Wylie-22)(Citation: Brubaker-Incontroller) [INCONTROLLER](https://attack.mitre.org/software/S1045) can obtain existing program logic from Omron PLCs by using either the program upload or backup functions available through the HTTP server.(Citation: Wylie-22) | relationship--b346eec8-de90-407c-b665-387086bb4553 | 29 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the CODESYS protocol to remotely connect to Schneider PLCs and perform maintenance functions on the device.(Citation: Wylie-22) [INCONTROLLER](https://attack.mitre.org/software/S1045) can use Telnet to upload payloads and execute commands on Omron PLCs. (Citation: Brubaker-Incontroller)(Citation: Dragos-Pipedream) The malware can also use HTTP-based CGI scripts (e.g., cpu.fcgi, ecat.fcgi) to gain administrative access to the device.(Citation: Wylie-22) | relationship--2867f491-919b-463f-b689-bb3ceb7ae99f | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can perform a UDP multicast scan of UDP port 27127 to identify Schneider PLCs that use that port for the NetManage protocol.(Citation: Dragos-Pipedream)(Citation: Wylie-22) [INCONTROLLER](https://attack.mitre.org/software/S1045) can use the FINS (Factory Interface Network Service) protocol to scan for and obtain MAC address associated with Omron devices.(Citation: CISA-AA22-103A)(Citation: Wylie-22) [INCONTROLLER](https://attack.mitre.org/software/S1045) has the ability to perform scans for TCP port 4840 to identify devices running OPC UA servers.(Citation: Wylie-22) | relationship--66af47d7-c430-4ac9-8020-fd79b7059037 | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) includes a library that creates Modbus connections with a device to request its device ID.(Citation: CISA-AA22-103A)(Citation: Wylie-22) | relationship--80a69b56-337d-446a-8167-8b9f63083c4f | 28 September 2022 | 13 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can remotely send commands to a malicious agent uploaded on Omron PLCs over HTTP or HTTPS.(Citation: CISA-AA22-103A) | relationship--0d4f2f88-e176-42c7-8258-52b345045662 | 28 September 2022 | 12 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can send custom Modbus commands to write register values on Schneider PLCs.(Citation: CISA-AA22-103A) [INCONTROLLER](https://attack.mitre.org/software/S1045) can send write tag values on OPC UA servers.(Citation: CISA-AA22-103A) | relationship--19c0d2bc-8de9-47c3-a1ee-63abc07c4348 | 28 September 2022 | 12 October 2022
S1045 | INCONTROLLER | malware--d3aa1058-b1b3-4c29-a3ba-9a9b90ccd93b | software | uses | T0859 | Valid Accounts | attack-pattern--cd2c76a4-5e23-4ca5-9c40-d5e0604f7101 | technique | [INCONTROLLER](https://attack.mitre.org/software/S1045) can brute force password-based authentication to Schneider PLCs over the CODESYS protocol (UDP port 1740).(Citation: CISA-AA22-103A) [INCONTROLLER](https://attack.mitre.org/software/S1045) can perform brute force guessing of passwords to OPC UA servers using a predefined list of passwords.(Citation: CISA-AA22-103A)(Citation: Wylie-22) | relationship--6681bc38-0b55-4714-b690-c609956b40bf | 28 September 2022 | 13 October 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0800 | Activate Firmware Update Mode | attack-pattern--19a71d1e-6334-4233-8260-b749cae37953 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) SIPROTEC DoS module places the victim device into firmware update mode. This is a legitimate use case under normal circumstances, but in this case is used the adversary to prevent the SIPROTEC from performing its designed protective functions. As a result the normal safeguards are disabled, leaving an unprotected link in the electric transmission. (Citation: Joe Slowik August 2019) | relationship--83c8c216-7ff7-4bd3-9db4-573469628d95 | 17 October 2018 | 25 September 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | [Industroyer](https://attack.mitre.org/software/S0604) automatically collects protocol object data to learn about control devices in the environment. (Citation: Anton Cherepanov, ESET June 2017) | relationship--c4122b58-f1b2-4656-a715-55016700bf75 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0803 | Block Command Message | attack-pattern--008b8f56-6107-48be-aa9f-746f927dbb61 | technique | In [Industroyer](https://attack.mitre.org/software/S0604) the first COM port from the configuration file is used for the actual communication and the two other COM ports are just opened to prevent other processes accessing them. Thus, the IEC 101 payload component is able to take over and maintain control of the RTU device. (Citation: Anton Cherepanov, ESET June 2017) | relationship--c785c026-4139-4c56-a6dd-cdd3ba75bab1 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0804 | Block Reporting Message | attack-pattern--3f1f4ccb-9be2-4ff8-8f69-dd972221169b | technique | [Industroyer](https://attack.mitre.org/software/S0604) uses the first COM port from the configuration file for the communication and the other two COM ports are opened to prevent other processes accessing them. This may block processes or operators from getting reporting messages from a device. (Citation: Anton Cherepanov, ESET June 2017) | relationship--648c6649-5861-4b43-a7e5-a9665bafb576 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0805 | Block Serial COM | attack-pattern--1c478716-71d9-46a4-9a53-fa5d576adb60 | technique | In [Industroyer](https://attack.mitre.org/software/S0604) the first COM port from the configuration file is used for the actual communication and the two other COM ports are just opened to prevent other processes accessing them. Thus, the IEC 101 payload component is able to take over and maintain control of the RTU device. (Citation: Anton Cherepanov, ESET June 2017) | relationship--8a604466-8437-4fe6-b6db-ec8fb05d702a | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) IEC 104 module has 3 modes available to perform its attack. These modes are range, shift, and sequence. The range mode operates in 2 stages. The first stage of range mode gathers Information Object Addresses (IOA) and sends select and execute packets to switch the state. The second stage of range mode has an infinite loop where it will switch the state of all of the previously discovered IOAs. Shift mode is similar to range mode, but instead of staying within the same range, it will add a shift value to the default range values. (Citation: Anton Cherepanov, ESET June 2017) | relationship--966b59c0-8641-432c-84f7-b2a712004d74 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | The name of the [Industroyer](https://attack.mitre.org/software/S0604) payload DLL is supplied by the attackers via a command line parameter supplied in one of the main backdoors execute a shell command commands. (Citation: Anton Cherepanov, ESET June 2017) | relationship--3be8045a-1f0d-4460-a76b-ae830e74c1e0 | 17 October 2018 | 12 October 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0884 | Connection Proxy | attack-pattern--d67adac8-e3b9-44f9-9e6d-6c2a7d69dbe4 | technique | [Industroyer](https://attack.mitre.org/software/S0604) attempts to connect with a hardcoded internal proxy on TCP 3128 [default Squid proxy]. If established, the backdoor attempts to reach an external C2 server via the internal proxy. (Citation: Dragos Inc. June 2017) | relationship--433539bf-cb17-4de1-9c0f-e579b041514f | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | [Industroyer](https://attack.mitre.org/software/S0604) has a destructive wiper that overwrites all ICS configuration files across the hard drives and all mapped network drives specifically targeting ABB PCM600 configuration files. (Citation: Dragos Inc. June 2017) | relationship--a1cbbdb5-30ad-4139-9784-e5a134f8d405 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0813 | Denial of Control | attack-pattern--e33c7ecc-5a38-497f-beb2-a9a2049a4c20 | technique | [Industroyer](https://attack.mitre.org/software/S0604) is able to block serial COM channels temporarily causing a denial of control. (Citation: Anton Cherepanov, ESET June 2017) | relationship--9902691c-aaf2-48a1-b1ca-cd6f652ae1c6 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | The [Industroyer](https://attack.mitre.org/software/S0604) SIPROTEC DoS module exploits the CVE-2015-5374 vulnerability in order to render a Siemens SIPROTEC device unresponsive. Once this vulnerability is successfully exploited, the target device stops responding to any commands until it is rebooted manually. (Citation: Anton Cherepanov, ESET June 2017) Once the tool is executed it sends specifically crafted packets to port 50,000 of the target IP addresses using UDP. The UDP packet contains the following 18 byte payload: 0x11 49 00 00 00 00 00 00 00 00 00 00 00 00 00 00 28 9E. (Citation: Anton Cherepanov, ESET June 2017) | relationship--50c20664-75dc-451e-b026-67b1d309e4b5 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0815 | Denial of View | attack-pattern--56ddc820-6cfb-407f-850b-52c035d123ac | technique | [Industroyer](https://attack.mitre.org/software/S0604) is able to block serial COM channels temporarily causing a denial of view. (Citation: Anton Cherepanov, ESET June 2017) | relationship--a04169ed-c16b-466b-80ef-22a11067f475 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0816 | Device Restart/Shutdown | attack-pattern--25dfc8ad-bd73-4dfd-84a9-3c3d383f76e9 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) SIPROTEC DoS module exploits the CVE-2015-5374 vulnerability in order to render a Siemens SIPROTEC device unresponsive. While the vulnerability does not directly cause the restart or shutdown of the device, the device must be restarted manually before it can resume operations. (Citation: Anton Cherepanov, ESET June 2017) | relationship--87c8ab74-576d-4962-b641-0762d374d1e8 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | [Industroyer](https://attack.mitre.org/software/S0604)'s data wiper component removes the registry image path throughout the system and overwrites all files, rendering the system unusable. (Citation: Anton Cherepanov, ESET June 2017) | relationship--a6d8b66d-fc10-404f-b0ae-e8c66506b818 | 17 October 2018 | 31 March 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0837 | Loss of Protection | attack-pattern--2bb4d762-bf4a-4bc3-9318-15cc6a354163 | technique | [Industroyer](https://attack.mitre.org/software/S0604) contained a module which leveraged a vulnerability in the Siemens SIPROTEC relays (CVE-2015-5374) to create a Denial of Service against automated protective relays. (Citation: Joe Slowik August 2019) | relationship--f347b4fe-d829-427d-851a-fff3393441db | 12 April 2021 | 14 April 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | [Industroyer](https://attack.mitre.org/software/S0604)'s data wiper component removes the registry image path throughout the system and overwrites all files, rendering the system unusable. (Citation: Anton Cherepanov, ESET June 2017) | relationship--9d6f9bba-dd79-4cb6-a0f3-1284e58a6236 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | [Industroyer](https://attack.mitre.org/software/S0604) toggles breakers to the open state utilizing unauthorized command messages. (Citation: Anton Cherepanov, ESET June 2017) | relationship--7c3b65e8-e8b7-4c3b-b27b-e216986d8976 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | [Industroyer](https://attack.mitre.org/software/S0604)'s OPC module can brute force values and will send out a 0x01 status which for the target systems equates to a Primary Variable Out of Limits misdirecting operators from understanding protective relay status. (Citation: Anton Cherepanov, ESET June 2017) | relationship--ca3c4d4b-cf53-4489-904f-8a220e421aeb | 17 October 2018 | 31 March 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | [Industroyer](https://attack.mitre.org/software/S0604)'s OPC and IEC 61850 protocol modules include the ability to send stVal requests to read the status of operational variables. (Citation: Anton Cherepanov, ESET June 2017) | relationship--83c29179-4805-403a-acf5-5151c4d2e556 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0840 | Network Connection Enumeration | attack-pattern--ea0c980c-5cf0-43a7-a049-59c4c207566e | technique | [Industroyer](https://attack.mitre.org/software/S0604) contains an IEC 61850 module that enumerates all connected network adapters to determine their TCP/IP subnet masks. (Citation: Anton Cherepanov, ESET June 2017) | relationship--841ec349-0f4c-43fa-89b8-ef3656497fc9 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) IEC 61850 payload component has the ability to discover relevant devices in the infected host's network subnet by attempting to connect on port 102.(Citation: Anton Cherepanov, ESET June 2017) [Industroyer](https://attack.mitre.org/software/S0604) contains an OPC DA module that enumerates all OPC servers using the `ICatInformation::EnumClassesOfCategories` method with `CATID_OPCDAServer20` category identifier and `IOPCServer::GetStatus` to identify the ones running. | relationship--1c831708-28c2-47ae-a158-39f1f7b73406 | 17 October 2018 | 29 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | The [Industroyer](https://attack.mitre.org/software/S0604) IEC 61850 component sends the domain-specific MMSgetNameList request to determine what logical nodes the device supports. It then searches the logical nodes for the CSW value, which indicates the device performs a circuit breaker or switch control function.(Citation: ESET Industroyer) [Industroyer](https://attack.mitre.org/software/S0604)'s OPC DA module also uses IOPCBrowseServerAddressSpace to look for items with the following strings: ctlSelOn, ctlOperOn, ctlSelOff, ctlOperOff, Pos and stVal.(Citation: ESET Industroyer) [Industroyer](https://attack.mitre.org/software/S0604) IEC 60870-5-104 module includes a range mode to discover Information Object Addresses (IOAs) by enumerating through each.(Citation: ESET Industroyer) | relationship--62e818b8-38e6-42ff-9424-9a327332eb2a | 29 September 2022 | 17 March 2023
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | [Industroyer](https://attack.mitre.org/software/S0604) has the capability to stop a service itself, or to login as a user and stop a service as that user. (Citation: Anton Cherepanov, ESET June 2017) | relationship--66f79019-d52c-46a6-b605-c2335d1d3d20 | 17 October 2018 | 23 September 2022
S0604 | Industroyer | malware--e401d4fe-f0c9-44f0-98e6-f93487678808 | software | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | Using its protocol payloads, [Industroyer](https://attack.mitre.org/software/S0604) sends unauthorized commands to RTUs to change the state of equipment. (Citation: Anton Cherepanov, ESET June 2017) | relationship--9fb2a9b2-3b25-4f77-9f7a-e832b2e5071a | 17 October 2018 | 23 September 2022
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0802 | Automated Collection | attack-pattern--3de230d4-3e42-4041-b089-17e1128feded | technique | [Industroyer2](https://attack.mitre.org/software/S1072) leverages a hardcoded list of remote-station IP addresses to iteratively initiate communications and collect information across multiple priority IEC-104 priority levels.(Citation: Industroyer2 Forescout July 2022) | relationship--6ff846b1-9444-45f1-837a-4eeeb16bdfe7 | 30 March 2023 | 30 March 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0806 | Brute Force I/O | attack-pattern--8e7089d3-fba2-44f8-94a8-9a79c53920c4 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) can iterate across a device’s IOAs to modify the ON/OFF value of a given IO state.(Citation: Industroyer2 Mandiant April 2022)(Citation: Industroyer2 Forescout July 2022) | relationship--2087b2b9-3b30-45be-abcd-4320bf0fa66b | 30 March 2023 | 06 April 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) modifies specified Information Object Addresses (IOAs) for specified Application Service Data Unit (ASDU) addresses to either the ON or OFF state.(Citation: Industroyer2 Mandiant April 2022)(Citation: Industroyer2 Forescout July 2022) | relationship--665587ee-1524-4334-9580-2b448c417542 | 30 March 2023 | 06 April 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | [Industroyer2](https://attack.mitre.org/software/S1072) uses a General Interrogation command to monitor the device’s Information Object Addresses (IOAs) and their IO state values.(Citation: Industroyer2 Forescout July 2022) | relationship--730580d4-d68c-407f-9d09-f379e9aefc7e | 30 March 2023 | 30 March 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) has the capability to poll a target device about its connection status, data transfer status, Common Address (CA), Information Object Addresses (IOAs), and IO state values across multiple priority levels.(Citation: Industroyer2 Forescout July 2022)(Citation: Industroyer2 ESET April 2022) | relationship--67e11f38-9f68-4989-8de3-da65af52063e | 30 March 2023 | 06 April 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) has the capability to terminate specified processes (i.e., PServiceControl.exe and PService_PDD.exe) and rename each process to prevent restart. These are defined through a hardcoded configuration.(Citation: Industroyer2 Mandiant April 2022) | relationship--54a977df-ca85-43b2-b2bc-96fdcd23aa9b | 30 March 2023 | 31 March 2023
S1072 | Industroyer2 | malware--6a0d0ea9-b2c4-43fe-a552-ac41a3009dc5 | software | uses | T0855 | Unauthorized Command Message | attack-pattern--40b300ba-f553-48bf-862e-9471b220d455 | technique | [Industroyer2](https://attack.mitre.org/software/S1072) is capable of sending command messages from the compromised device to target remote stations to open data channels, retrieve the location and values of Information Object Addresses (IOAs), and modify the IO state values through Select Before Operate I/O, Select/Execute, and Invert Default State operations.(Citation: Industroyer2 Mandiant April 2022)(Citation: Industroyer2 Forescout July 2022) | relationship--6a5922e1-e282-464d-9e71-ce2c2ed44908 | 30 March 2023 | 06 April 2023
S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | uses | T0809 | Data Destruction | attack-pattern--493832d9-cea6-4b63-abe7-9a65a6473675 | technique | [KillDisk](https://attack.mitre.org/software/S0607) is able to delete system files to make the system unbootable and targets 35 different types of files for deletion. (Citation: Anton Cherepanov) | relationship--b252a076-6d4e-49f5-95ac-16264ef05b1d | 14 December 2017 | 12 October 2022
S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | uses | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | [KillDisk](https://attack.mitre.org/software/S0607) deletes application, security, setup, and system event logs from Windows systems. (Citation: Anton Cherepanov) | relationship--ab8e129c-5411-4784-9194-068fa915da23 | 14 December 2017 | 12 October 2022
S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | [KillDisk](https://attack.mitre.org/software/S0607) erases the master boot record (MBR) and system logs, leaving the system unusable. (Citation: Booz Allen Hamilton) | relationship--04bf72de-75ba-4d95-ad24-f93ad835180c | 14 December 2017 | 12 October 2022
S0607 | KillDisk | malware--e221eb77-1502-4129-af1d-fe1ad55e7ec6 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | [KillDisk](https://attack.mitre.org/software/S0607) looks for and terminates two non-standard processes, one of which is an ICS application. (Citation: Anton Cherepanov) | relationship--b452a076-6d4e-49f5-95ac-16264ef05b1d | 14 December 2017 | 12 October 2022
S0372 | LockerGoga | malware--5af7a825-2d9f-400d-931a-e00eb9e27f48 | software | uses | T0827 | Loss of Control | attack-pattern--a81696ef-c106-482c-8f80-59c30f2569fb | technique | Some of Norsk Hydro's production systems were impacted by a [LockerGoga](https://attack.mitre.org/software/S0372) infection. This resulted in a loss of control which forced the company to switch to manual operations. (Citation: Kevin Beaumont) (Citation: Hydro) | relationship--b5ab26e2-eb90-4f19-b35a-b8a0a5438961 | 14 December 2017 | 12 October 2022
S0372 | LockerGoga | malware--5af7a825-2d9f-400d-931a-e00eb9e27f48 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | While Norsk Hydro attempted to recover from a [LockerGoga](https://attack.mitre.org/software/S0372) infection, most of its 160 manufacturing locations switched to manual (non-IT driven) operations. Manual operations can result in a loss of productivity. (Citation: Kevin Beaumont)(Citation: Hydro) | relationship--46bc86e4-e20b-4778-80d2-8891039e6fb4 | 14 December 2017 | 12 October 2022
S0372 | LockerGoga | malware--5af7a825-2d9f-400d-931a-e00eb9e27f48 | software | uses | T0829 | Loss of View | attack-pattern--138979ba-0430-4de6-a128-2fc0b056ba36 | technique | Some of Norsk Hydro's production systems were impacted by a [LockerGoga](https://attack.mitre.org/software/S0372) infection. This resulted in a loss of view which forced the company to switch to manual operations. (Citation: Kevin Beaumont) (Citation: Hydro) | relationship--7a55fc66-0d5c-4ef6-af28-d4a4bb84381d | 14 December 2017 | 12 October 2022
S0368 | NotPetya | malware--5719af9d-6b16-46f9-9b28-fb019541ddbb | software | uses | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | [NotPetya](https://attack.mitre.org/software/S0368) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks. (Citation: Joe Slowik April 2019) | relationship--6603a100-d655-4e6b-8d38-73c11b89dde4 | 26 March 2019 | 12 October 2022
S0368 | NotPetya | malware--5719af9d-6b16-46f9-9b28-fb019541ddbb | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [NotPetya](https://attack.mitre.org/software/S0368) can move laterally through industrial networks by means of the SMB service. (Citation: Joe Slowik April 2019) | relationship--6258c355-677c-452d-b1fc-27767232437b | 26 March 2019 | 12 October 2022
S0368 | NotPetya | malware--5719af9d-6b16-46f9-9b28-fb019541ddbb | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | [NotPetya](https://attack.mitre.org/software/S0368) disrupted manufacturing facilities supplying vaccines, resulting in a halt of production and the inability to meet demand for specific vaccines. (Citation: David Voreacos, Katherine Chinglinsky, Riley Griffin December 2019) | relationship--7258c355-677c-452d-b1fc-27767232437b | 26 March 2019 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) stops the execution of the user program on the target to enable the transfer of its own code. The worm then copies itself to the target and subsequently starts the target PLC again. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--a4c81fe6-1ad9-4bba-a415-a3c099eaa2be | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0814 | Denial of Service | attack-pattern--1b22b676-9347-4c55-9a35-ef0dc653db5b | technique | The execution on the PLC can be stopped by violating the cycle time limit. The [PLC-Blaster](https://attack.mitre.org/software/S1006) implements an endless loop triggering an error condition within the PLC with the impact of a DoS. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--535c5160-17e0-44eb-9f4b-1a8e216b56a2 | 17 October 2018 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) may manipulate any outputs of the PLC. Using the POU POKE any value within the process image may be modified. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--6fa3aee4-2a29-4c0f-9e61-1f7df5eccc00 | 17 October 2018 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006)'s code is stored in OB9999. The original code on the target is untouched. The OB is automatically detected by the PLC and executed. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--20f66fab-7a08-4707-ac79-92dac5acd11d | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) copies itself to various Program Organization Units (POU) on the target device. The POUs include the Data Block, Function, and Function Block. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--9515f24c-1c33-4197-b9c9-b9992bc696ca | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) uses the system function blocks TCON and TDISCON to initiate and destroy TCP connections to arbitrary systems. Buffers may be sent and received on these connections with TRCV und TSEND system function blocks. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--21041206-da58-45c7-adb0-db07caebdcb6 | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) utilizes the PLC communication and management API to load executable Program Organization Units. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--31897c41-1d47-4a34-b531-21c3f74651a8 | 13 April 2021 | 12 October 2022
S1006 | PLC-Blaster | malware--4dcff507-5af8-47ce-964a-8d9569e9ccfe | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | [PLC-Blaster](https://attack.mitre.org/software/S1006) scans the network to find other Siemens S7 PLC devices to infect. It locates these devices by checking for a service listening on TCP port 102. (Citation: Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016) | relationship--5c0bdf4c-233f-42cd-8900-2a5cc8c9387c | 17 October 2018 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | The [REvil](https://attack.mitre.org/software/S0496) malware gained access to an organizations network and encrypted sensitive files used by OT equipment. (Citation: Selena Larson, Camille Singleton December 2020) | relationship--ab306654-2abb-4983-8d30-df4058adb06c | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | [REvil](https://attack.mitre.org/software/S0496) searches for whether the Ahnlab autoup.exe service is running on the target system and injects its payload into this existing process. (Citation: Tom Fakterman August 2019) | relationship--5e099568-fb5c-4f58-af7e-4e1b7a9d1128 | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | [REvil](https://attack.mitre.org/software/S0496) uses the SMB protocol to encrypt files located on remotely connected file shares. (Citation: Max Heinemeyer February 2020) | relationship--e323dee4-a896-4a82-85f5-d51d311b0437 | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | [REvil](https://attack.mitre.org/software/S0496) utilizes JavaScript, WScript, and PowerShell scripts to execute. The malicious JavaScript attachment has an obfuscated PowerShell script that executes the malware. (Citation: Tom Fakterman August 2019) | relationship--ee1bf429-2c7c-4eb6-acca-e758522baf2e | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0881 | Service Stop | attack-pattern--063b5b92-5361-481a-9c3f-95492ed9a2d8 | technique | [REvil](https://attack.mitre.org/software/S0496) searches for all processes listed in the prc field within its configuration file and then terminates each process. (Citation: McAfee Labs October 2019) | relationship--309e4558-e591-4d03-9bb9-07d30acf011f | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [REvil](https://attack.mitre.org/software/S0496) sends HTTPS POST messages with randomly generated URLs to communicate with a remote server. (Citation: Tom Fakterman August 2019) (Citation: SecureWorks September 2019) | relationship--c90cfddb-253b-41c8-9057-2abde6f8aa6d | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0882 | Theft of Operational Information | attack-pattern--b7e13ee8-182c-4f19-92a4-a88d7d855d54 | technique | [REvil](https://attack.mitre.org/software/S0496) sends exfiltrated data from the victims system using HTTPS POST messages sent to the C2 system. (Citation: McAfee Labs October 2019) (Citation: SecureWorks September 2019) | relationship--6ed07095-c23a-4676-807f-a544deaeb274 | 12 April 2021 | 12 October 2022
S0496 | REvil | malware--ac61f1f9-7bb1-465e-9b8a-c2ce8e88baf5 | software | uses | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | [REvil](https://attack.mitre.org/software/S0496) initially executes when the user clicks on a JavaScript file included in the phishing emails .zip attachment. (Citation: Tom Fakterman August 2019) | relationship--1fd4cf4e-a26c-4fe5-a7fd-f49b8aea8437 | 12 April 2021 | 12 October 2022
S0446 | Ryuk | malware--a020a61c-423f-4195-8c46-ba1d21abba37 | software | uses | T0828 | Loss of Productivity and Revenue | attack-pattern--63b6942d-8359-4506-bfb3-cf87aa8120ee | technique | An enterprise resource planning (ERP) manufacturing server was lost to the [Ryuk](https://attack.mitre.org/software/S0446) attack. The manufacturing process had to rely on paper and existing orders to keep the shop floor open. (Citation: Kelly Jackson Higgins) | relationship--383e242a-72d4-4b40-8905-888595c34919 | 14 December 2017 | 12 October 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0807 | Command-Line Interface | attack-pattern--24a9253e-8948-4c98-b751-8e2aee53127c | technique | [Stuxnet](https://attack.mitre.org/software/S0603) will store and execute SQL code that will extract and execute Stuxnet from the saved CAB file using xp_cmdshell with the following command: `set @s = master..xp _ cmdshell extrac32 /y +@t+ +@t+x; exec(@s);` (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--6baa9172-04e4-416d-a009-668cda23fd5d | 08 October 2021 | 19 October 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) attempts to contact command and control servers on port 80 to send basic information about the computer it has compromised. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--bcece7ce-91b5-40b3-b87a-25cab3600e5c | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | [Stuxnet](https://attack.mitre.org/software/S0603) executes malicious SQL commands in the WinCC database server to propagate to remote systems. The malicious SQL commands include xp_cmdshell, sp_dumpdbilog, and sp_addextendedproc. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--be532c78-daf5-431b-adae-ab11af395513 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0891 | Hardcoded Credentials | attack-pattern--c9a8d958-fcdb-40d2-af4c-461c8031651a | technique | [Stuxnet](https://attack.mitre.org/software/S0603) uses a hardcoded password in the WinCC software's database server as one of the mechanisms used to propagate to nearby systems. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--874752f4-59a2-46e9-ae28-befe0142b223 | 14 December 2017 | 30 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | [Stuxnet](https://attack.mitre.org/software/S0603) modifies the Import Address Tables DLLs to hook specific APIs that are used to open project files. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--53a54e4a-2b38-4b0c-8f60-252a68767443 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0877 | I/O Image | attack-pattern--53a48c74-0025-45f4-b04a-baa853df8204 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) copies the input area of an I/O image into data blocks with a one second interval between copies, forming a 21 second recording of the input area. The input area contains information being passed to the PLC from a peripheral. For example, the current state of a valve or the temperature of a device. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--28afd84d-a53e-4b2f-9bee-133f7da6982a | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [Stuxnet](https://attack.mitre.org/software/S0603) sends an SQL statement that creates a table and inserts a binary value into the table. The binary value is a hex string representation of the main Stuxnet DLL as an executable file (formed using resource 210) and an updated configuration data block. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--327916f7-fe5d-4858-adeb-f72f74c60c25 | 08 October 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0835 | Manipulate I/O Image | attack-pattern--36e9f5bc-ac13-4da4-a2f4-01f4877d9004 | technique | When the peripheral output is written to, sequence C intercepts the output and ensures it is not written to the process image output. The output is the instructions the PLC sends to a device to change its operating behavior. By intercepting the peripheral output, [Stuxnet](https://attack.mitre.org/software/S0603) prevents an operator from noticing unauthorized commands sent to the peripheral. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--f0c81c9f-2fb7-4e7d-98ed-c75e3be7d962 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0831 | Manipulation of Control | attack-pattern--1af9e3fd-2bcc-414d-adbd-fe3b95c02ca1 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) can reprogram a PLC and change critical parameters in such a way that legitimate commands can be overridden or intercepted. In addition, Stuxnet can apply inappropriate command sequences or parameters to cause damage to property. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--c6520346-fe47-44ce-af75-d99004ac2977 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0832 | Manipulation of View | attack-pattern--4c2e1408-9d68-4187-8e6b-a77bc52700ec | technique | [Stuxnet](https://attack.mitre.org/software/S0603) manipulates the view of operators replaying process input and manipulating the I/O image to evade detection and inhibit protection functions. (Citation: Langer Stuxnet) (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--e257913e-40ba-4a05-ba97-0c3175c966b5 | 14 December 2017 | 17 March 2023
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) renames s7otbxdx.dll, a dll responsible for handling communications with a PLC. It replaces this dll file with its own version that allows it to intercept any calls that are made to access the PLC. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--0e29f62d-4ffc-47ec-9623-72f874fbe905 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) infects OB1 so that its malicious code sequence is executed at the start of a cycle. It also infects OB35. OB35 acts as a watchdog, and on certain conditions, it can stop the execution of OB1. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--ccae6e5d-8a9e-4bab-ae77-26a2bd722f67 | 13 April 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0836 | Modify Parameter | attack-pattern--097924ce-a9a9-4039-8591-e0deedfb8722 | technique | In states 3 and 4 [Stuxnet](https://attack.mitre.org/software/S0603) sends two network bursts (done through the DP_SEND primitive). The data in the frames are instructions for the frequency converter drives. For example one of the frames contains records that change the maximum frequency (the speed at which the motor will operate). The frequency converter drives consist of parameters, which can be remotely configured via Profibus. One can write new values to these parameters changing the behavior of the device. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--50b3247a-ea71-455e-b299-f00666c05146 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0889 | Modify Program | attack-pattern--fc5fda7e-6b2c-4457-b036-759896a2efa2 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) infects PLCs with different code depending on the characteristics of the target system. An infection sequence consists of code blocks and data blocks that will be downloaded to the PLC to alter its behavior. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--cb38425c-646d-4bc8-bdea-e6cc630c3034 | 13 April 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0801 | Monitor Process State | attack-pattern--2d0d40ad-22fa-4cc8-b264-072557e1364b | technique | [Stuxnet](https://attack.mitre.org/software/S0603) examines fields recorded by the DP_RECV monitor to determine if the target system is in a particular state of operation. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--2fd13fc0-e3f0-4099-ab20-d19ba6bcd4e0 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | [Stuxnet](https://attack.mitre.org/software/S0603) calls system function blocks which are part of the operating system running on the PLC. Theyre used to execute system tasks, such as reading the system clock (SFC1) and generating data blocks on the fly. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--3d005ed8-77d3-4fed-9dd5-7e39ba8cb50a | 13 April 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | DP_RECV is the name of a standard function block used by network coprocessors. It is used to receive network frames on the Profibus a standard industrial network bus used for distributed I/O. The original block is copied to FC1869, and then replaced by a malicious block. Each time the function is used to receive a packet, the malicious [Stuxnet](https://attack.mitre.org/software/S0603) block takes control: it will call the original DP_RECV in FC1869 and then perform postprocessing on the packet data. The replaced DP_RECV block (later on referred to as the DP_RECV monitor) is meant to monitor data sent by the frequency converter drives to the 315-2 CPU via CP 342-5 Profibus communication modules. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--f29ecf69-1753-44bb-9b80-1025f49cadda | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | [Stuxnet](https://attack.mitre.org/software/S0603)'s infection sequence consists of code blocks and data blocks that will be downloaded to the PLC to alter its behavior. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--7c893581-c847-495a-aa93-9d98c516e1ae | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0873 | Project File Infection | attack-pattern--e72425f8-9ae6-41d3-bfdb-e1b865e60722 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) copies itself into Step 7 projects in such a way that it automatically executes when the Step 7 project is loaded. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--dfe43fa1-ffc2-4c6c-a91d-f2ca55f21ccb | 14 December 2017 | 12 October 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0886 | Remote Services | attack-pattern--e1f9cdd2-9511-4fca-90d7-f3e92cfdd0bf | technique | [Stuxnet](https://attack.mitre.org/software/S0603) executes malicious SQL commands in the WinCC database server to propagate to remote systems. The malicious SQL commands include xp_cmdshell, sp_dumpdbilog, and sp_addextendedproc. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--eaeb3c8d-9d91-4eb0-8049-5cb99e141026 | 08 October 2021 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0888 | Remote System Information Discovery | attack-pattern--2fedbe69-581f-447d-8a78-32ee7db939a9 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) enumerates and parses the System Data Blocks (SDB) using the s7blk_findfirst and s7blk_findnext API calls in s7otbxdx.dll. Stuxnet must find an SDB with the DWORD at offset 50h equal to 0100CB2Ch. This specifies that the system uses the Profibus communications processor module CP 342-5. In addition, specific values are searched for and counted: 7050h and 9500h. 7050h is assigned to part number KFC750V3 which appears to be a frequency converter drive (also known as variable frequency drive) manufactured by Fararo Paya in Teheran, Iran. 9500h is assigned to Vacon NX frequency converter drives manufactured by Vacon based in Finland.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) [Stuxnet](https://attack.mitre.org/software/S0603) was specifically targeting CPUs 6ES7-315-2 (Series 300) with special system data block characteristics for sequence A or B and 6ES7-315-2 for sequence C. The PLC type can also be checked using the s7ag_read_szl API.(Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--1d35c947-447f-4693-9ab0-32dff56e664e | 13 April 2021 | 29 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0847 | Replication Through Removable Media | attack-pattern--c267bbee-bb59-47fe-85e0-3ed210337c21 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) was able to self-replicate by being spread through removable drives. A willing insider or unknown third party, such as a contractor, may have brought the removable media into the target environment. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) The earliest version of Stuxnet relied on physical installation, infecting target systems when an infected configuration file carried by a USB stick was opened. (Citation: Langer Stuxnet) | relationship--82b20c35-88c6-49aa-8241-a59512b17b74 | 14 December 2017 | 17 March 2023
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0851 | Rootkit | attack-pattern--3b6b9246-43f8-4c69-ad7a-2b11cfe0a0d9 | technique | One of [Stuxnet](https://attack.mitre.org/software/S0603)'s rootkits is contained entirely in the fake s7otbxdx.dll. In order to continue existing undetected on the PLC it needs to account for at least the following situations: read requests for its own malicious code blocks, read requests for infected blocks (OB1, OB35, DP_RECV), and write requests that could overwrite Stuxnets own code. Stuxnet contains code to monitor and intercept these types of requests. The rootkit modifies these requests so that Stuxnets PLC code is not discovered or damaged. (Citation: Langer Stuxnet) | relationship--f130282b-f681-455f-966b-55829842be92 | 14 December 2017 | 17 March 2023
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [Stuxnet](https://attack.mitre.org/software/S0603) uses a thread to monitor a data block DB890 of sequence A or B. This thread is constantly running and probing this block (every 5 minutes). On an infected PLC, if block DB890 is found and contains a special magic value (used by Stuxnet to identify his own block DB890), this blocks data can be read and written. This thread is likely used to optimize the way sequences A and B work, and modify their behavior when the Step7 editor is opened. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--bc383819-2e40-49b4-bea9-95eb5d418877 | 14 December 2017 | 20 September 2022
S0603 | Stuxnet | malware--088f1d6e-0783-47c6-9923-9c79b2af43d4 | software | uses | T0863 | User Execution | attack-pattern--2736b752-4ec5-4421-a230-8977dea7649c | technique | [Stuxnet](https://attack.mitre.org/software/S0603) infects DLL's associated with the WinCC Simatic manager which are responsible for opening project files. If a user opens an uninfected project file using a compromised manager, the file will be infected with Stuxnet code. If an infected project is opened with the Simatic manager, the modified data file will trigger a search for the `xyz.dll` file. If the `xyz.dll` file is not found in any of the specified locations, the malicious DLL will be loaded and executed by the manager. (Citation: Nicolas Falliere, Liam O Murchu, Eric Chien February 2011) | relationship--8a06c15b-b7e5-4374-9265-8d9020e126cd | 14 October 2021 | 19 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0858 | Change Operating Mode | attack-pattern--2883c520-7957-46ca-89bd-dab1ad53b601 | technique | [Triton](https://attack.mitre.org/software/S1009) has the ability to halt or run a program through the TriStation protocol. TsHi.py contains instances of halt and run functions being executed. (Citation: MDudek-ICS) | relationship--74b66248-2cb6-46ea-b52c-c7d60c170f3f | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0885 | Commonly Used Port | attack-pattern--e6c31185-8040-4267-83d3-b217b8a92f07 | technique | [Triton](https://attack.mitre.org/software/S1009) uses TriStations default UDP port, 1502, to communicate with devices. (Citation: MDudek-ICS) | relationship--8b2d82aa-75fc-4d6d-bb4b-9f600bd211fd | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0868 | Detect Operating Mode | attack-pattern--2aa406ed-81c3-4c1d-ba83-cfbee5a2847a | technique | [Triton](https://attack.mitre.org/software/S1009) contains a file named TS_cnames.py which contains default definitions for program state (TS_progstate). Program state is referenced in TsHi.py.(Citation: MDudek-ICS) [Triton](https://attack.mitre.org/software/S1009) contains a file named TS_cnames.py which contains default definitions for key state (TS_keystate). Key state is referenced in TsHi.py.(Citation: MDudek-ICS) | relationship--9db1ecfe-72eb-42da-a09e-746663a53854 | 18 April 2018 | 29 September 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0871 | Execution through API | attack-pattern--5a2610f6-9fff-41e1-bc27-575ca20383d4 | technique | [Triton](https://attack.mitre.org/software/S1009) leverages a reconstructed TriStation protocol within its framework to trigger APIs related to program download, program allocation, and program changes. (Citation: Jos Wetzels January 2018) | relationship--d72e7d01-56be-4fbd-8957-3384533ba83b | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0820 | Exploitation for Evasion | attack-pattern--9f947a1c-3860-48a8-8af0-a2dfa3efde03 | technique | [Triton](https://attack.mitre.org/software/S1009) disables a firmware RAM/ROM consistency check after injects a payload (imain.bin) into the firmware memory region. (Citation: DHS CISA February 2019) (Citation: ICS-CERT December 2018) (Citation: Schneider Electric January 2018) Triconex systems include continuous means of detection including checksums for firmware and program integrity, memory and memory reference integrity, and configuration. (Citation: The Office of Nuclear Reactor Regulation) | relationship--ea50253a-3220-458b-b810-ad032f2b182f | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0890 | Exploitation for Privilege Escalation | attack-pattern--cfe68e93-ce94-4c0f-a57d-3aa72cedd618 | technique | [Triton](https://attack.mitre.org/software/S1009) leverages a previously-unknown vulnerability affecting Tricon MP3008 firmware versions 10.010.4 allows an insecurely-written system call to be exploited to achieve an arbitrary 2-byte write primitive, which is then used to gain supervisor privileges. (Citation: DHS CISA February 2019) | relationship--591620d3-5549-49db-9080-43f86a68a590 | 13 April 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0874 | Hooking | attack-pattern--ab390887-afc0-4715-826d-b1b167d522ae | technique | [Triton](https://attack.mitre.org/software/S1009)'s injector, inject.bin, changes the function pointer of the 'get main processor diagnostic data' TriStation command to the address of imain.bin so that it is executed prior to the normal handler. (Citation: Jos Wetzels January 2018) | relationship--ccc67bb3-acc3-4294-81b3-4a0d972f2dd7 | 13 April 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0872 | Indicator Removal on Host | attack-pattern--53a26eee-1080-4d17-9762-2027d5a1b805 | technique | [Triton](https://attack.mitre.org/software/S1009) would reset the controller to the previous state over TriStation and if this failed it would write a dummy program to memory in what was likely an attempt at anti-forensics. (Citation: Jos Wetzels January 2018) | relationship--56dcc2d7-5243-4a5d-a556-8723642e98a4 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0880 | Loss of Safety | attack-pattern--5fa00fdd-4a55-4191-94a0-564181d7fec2 | technique | [Triton](https://attack.mitre.org/software/S1009) has the capability to reprogram the SIS logic to allow unsafe conditions to persist or reprogram the SIS to allow an unsafe state while using the DCS to create an unsafe state or hazard. (Citation: Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017) | relationship--d8354850-bd4c-4bd9-a585-b107f5f1398f | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0849 | Masquerading | attack-pattern--ba203963-3182-41ac-af14-7e7ebc83cd61 | technique | [Triton](https://attack.mitre.org/software/S1009)'s injector, inject.bin, masquerades as a standard compiled PowerPC program for the Tricon. (Citation: DHS CISA February 2019) [Triton](https://attack.mitre.org/software/S1009) was configured to masquerade as trilog.exe, which is the Triconex software for analyzing SIS logs.(Citation: FireEye TRITON) | relationship--350814da-5c36-42f9-8e58-8f9534e6ce0a | 18 April 2018 | 29 September 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0821 | Modify Controller Tasking | attack-pattern--09a61657-46e1-439e-b3ed-3e4556a78243 | technique | [Triton](https://attack.mitre.org/software/S1009)'s argument-setting and inject.bin shellcode are added to the program table on the Tricon so that they are executed by the firmware once each cycle. (Citation: DHS CISA February 2019) (Citation: Jos Wetzels January 2018) | relationship--63ca148e-12c9-4090-b51e-a8fb7a847a2a | 13 April 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0834 | Native API | attack-pattern--b52870cc-83f3-473c-b895-72d91751030b | technique | [Triton](https://attack.mitre.org/software/S1009)'s imain.bin payload takes commands from the TsHi.ExplReadRam(Ex), TsHi.ExplWriteRam(Ex) and TsHi.ExplExec functions to perform operations on controller memory and registers using syscalls written in PowerPC shellcode. (Citation: Jos Wetzels January 2018) | relationship--13809e98-1d74-4c39-b882-9d523c76cbde | 13 April 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0843 | Program Download | attack-pattern--be69c571-d746-4b1f-bdd0-c0c9817e9068 | technique | [Triton](https://attack.mitre.org/software/S1009) leveraged the TriStation protocol to download programs onto Triconex Safety Instrumented System. (Citation: Jos Wetzels January 2018) | relationship--1f8abf6f-0dd0-4449-b555-733fe7296177 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0845 | Program Upload | attack-pattern--3067b85e-271e-4bc5-81ad-ab1a81d411e3 | technique | [Triton](https://attack.mitre.org/software/S1009) calls the SafeAppendProgramMod to transfer its payloads to the Tricon. Part of this call includes preforming a program upload. (Citation: MDudek-ICS) | relationship--a946c9b1-5b89-44c9-b617-3412ffda34b9 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0846 | Remote System Discovery | attack-pattern--d5a69cfb-fc2a-46cb-99eb-74b236db5061 | technique | [Triton](https://attack.mitre.org/software/S1009) uses a Python script that is capable of detecting Triconex controllers on the network by sending a specific UDP broadcast packet over port 1502. (Citation: DHS CISA February 2019) | relationship--351e19c4-c16e-493a-9800-a433107aacf1 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0853 | Scripting | attack-pattern--2dc2b567-8821-49f9-9045-8740f3d0b958 | technique | [Triton](https://attack.mitre.org/software/S1009) communicates with Triconex controllers using a custom component framework written entirely in Python. The modules that implement the TriStation communication protocol and other supporting components are found in a separate file -- library.zip -- the main script that employs this functionality is compiled into a standalone py2exe Windows executable -- trilog.exe which includes a Python environment. (Citation: DHS CISA February 2019) | relationship--709c4e40-c5c6-405b-bc3d-0adfea40ccd4 | 18 April 2018 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0869 | Standard Application Layer Protocol | attack-pattern--e076cca8-2f08-45c9-aff7-ea5ac798b387 | technique | [Triton](https://attack.mitre.org/software/S1009) can communicate with the implant utilizing the TriStation 'get main processor diagnostic data' command and looks for a specifically crafted packet body from which it extracts a command value and its arguments. (Citation: Jos Wetzels January 2018) | relationship--f584a257-c22a-434b-aa2d-6220987821ab | 13 October 2021 | 12 October 2022
S1009 | Triton | malware--80099a91-4c86-4bea-9ccb-dac55d61960e | software | uses | T0857 | System Firmware | attack-pattern--b9160e77-ea9e-4ba9-b1c8-53a3c466b13d | technique | [Triton](https://attack.mitre.org/software/S1009) is able to read, write and execute code in memory on the safety controller at an arbitrary address within the devices firmware region. This allows the malware to make changes to the running firmware in memory and modify how the device operates. (Citation: DHS CISA February 2019) | relationship--93e24e03-6425-4ee8-99bb-c3a662c6cdce | 18 April 2018 | 12 October 2022
S1010 | VPNFilter | malware--6108f800-10b8-4090-944e-be579f01263d | software | uses | T0830 | Adversary-in-the-Middle | attack-pattern--9a505987-ab05-4f46-a9a6-6441442eec3b | technique | The [VPNFilter](https://attack.mitre.org/software/S1010)'s ssler module configures the device's iptables to redirect all traffic destined for port 80 to its local service listening on port 8888. Any outgoing web requests on port 80 are now intercepted by ssler and can be inspected by the ps module and manipulated before being sent to the legitimate HTTP service. (Citation: William Largent June 2018) (Citation: Carl Hurd March 2019) | relationship--c84e39ab-30c1-40e3-95a8-fcbb271e913c | 06 May 2022 | 12 October 2022
S1010 | VPNFilter | malware--6108f800-10b8-4090-944e-be579f01263d | software | uses | T0842 | Network Sniffing | attack-pattern--38213338-1aab-479d-949b-c81b66ccca5c | technique | The [VPNFilter](https://attack.mitre.org/software/S1010) packet sniffer looks for basic authentication as well as monitors ICS traffic, and is specific to the TP-LINK R600-VPN. The malware uses a raw socket to look for connections to a pre-specified IP address, only looking at TCP packets that are 150 bytes or larger. Packets that are not on port 502, are scanned for BasicAuth, and that information is logged. This may have allowed credential harvesting from communications between devices accessing a modbus-enabled HMI. (Citation: William Largent June 2018) (Citation: Carl Hurd March 2019) | relationship--cad91f87-7cc7-4771-8c7b-1599793ed3c1 | 17 October 2018 | 12 October 2022
S0366 | WannaCry | malware--75ecdbf1-c2bb-4afc-a3f9-c8da4de8c661 | software | uses | T0866 | Exploitation of Remote Services | attack-pattern--85a45294-08f1-4539-bf00-7da08aa7b0ee | technique | [WannaCry](https://attack.mitre.org/software/S0366) initially infected IT networks, but by means of an exploit (particularly the SMBv1-targeting MS17-010 vulnerability) spread to industrial networks. (Citation: Joe Slowik April 2019) | relationship--c59a3d89-c8fa-4c5d-813e-f4495d892d1a | 25 March 2019 | 12 October 2022
S0366 | WannaCry | malware--75ecdbf1-c2bb-4afc-a3f9-c8da4de8c661 | software | uses | T0867 | Lateral Tool Transfer | attack-pattern--ead7bd34-186e-4c79-9a4d-b65bcce6ed9d | technique | [WannaCry](https://attack.mitre.org/software/S0366) can move laterally through industrial networks by means of the SMB service. (Citation: Joe Slowik April 2019) | relationship--d50a3d89-c8fa-4c5d-813e-f4495d892d1a | 25 March 2019 | 12 October 2022

## datasources
name | ID | STIX ID | description | collection layers | platforms | created | modified | type | version | url | contributors
Application Log | DS0015 | x-mitre-data-source--40269753-26bd-437b-986e-159c66dec5e4 | Events collected by third-party services such as mail servers, web applications, or other appliances (not by the native OS or platform)(Citation: Confluence Logs) | Cloud Control Plane, Host | Google Workspace, IaaS, Linux, Office 365, SaaS, Windows, macOS | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0015
Application Log: Application Log Content |  | x-mitre-data-component--9c2fa0ae-7abc-485a-97f6-699e3b6cf9fa | Logging, messaging, and other artifacts provided by third-party services (ex: metrics, errors, and/or alerts from mail/web applications) |  |  | 20 October 2021 |  | datacomponent | 1.0
Asset | DS0039 | x-mitre-data-source--b1717cb4-d536-4e2b-b5e5-07e67e26183c | Data sources with information about the set of devices found within the network, along with their current software and configurations | Host |  | 11 May 2022 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0039
Asset: Asset Inventory |  | x-mitre-data-component--b05a614b-033c-4578-b4f2-c63a9feee706 | This includes sources of current and expected devices on the network, including the manufacturer, model, and necessary identifiers (e.g., IP and hardware addresses) |  |  | 23 September 2022 |  | datacomponent | 1.0
Asset: Software |  | x-mitre-data-component--8ed4e6d0-56d7-4e6b-8fa6-41f41631f30d | This includes sources of current and expected software or application programs deployed to a device, along with information on the version and patch level for vendor products, full source code for any application programs, and unique identifiers (e.g., hashes, signatures). |  |  | 23 September 2022 |  | datacomponent | 1.0
Command | DS0017 | x-mitre-data-source--73691708-ffb5-4e29-906d-f485f6fa7089 | A directive given to a computer program, acting as an interpreter of some kind, in order to perform a specific task(Citation: Confluence Linux Command Line)(Citation: Audit OSX) | Container, Host | Android, Containers, Linux, Network, Windows, iOS, macOS | 20 October 2021 |  | datasource | 1.1 | https://attack.mitre.org/datasources/DS0017 | Austin Clark, @c2defense; Center for Threat-Informed Defense (CTID)
Command: Command Execution |  | x-mitre-data-component--685f917a-e95e-4ba0-ade1-c7d354dae6e0 | The execution of a line of text, potentially with arguments, created from program code (e.g. a cmdlet executed via powershell.exe, interactive commands like >dir, shell executions, etc. ) |  |  | 20 October 2021 |  | datacomponent | 1.1
Drive | DS0016 | x-mitre-data-source--61bbbf27-f7c3-46ba-a6bc-48ae76928065 | A non-volatile data storage device (hard drive, floppy disk, USB flash drive) with at least one formatted partition, typically mounted to the file system and/or assigned a drive letter(Citation: Sysmon EID 9) | Host | Linux, Windows, macOS | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0016 | Center for Threat-Informed Defense (CTID)
Drive: Drive Creation |  | x-mitre-data-component--3d6e6b3b-4aa8-40e1-8c47-91db0f313d9f | Initial construction of a drive letter or mount point to a data storage device |  |  | 20 October 2021 |  | datacomponent | 1.0
Drive: Drive Modification |  | x-mitre-data-component--4dcd8ba3-2075-4f8b-941e-39884ffaac08 | Changes made to a drive letter or mount point of a data storage device |  |  | 20 October 2021 |  | datacomponent | 1.0
File | DS0022 | x-mitre-data-source--509ed41e-ca42-461e-9058-24602256daf9 | A computer resource object, managed by the I/O system, for storing data (such as images, text, videos, computer programs, or any wide variety of other media).(Citation: Microsoft File Mgmt) | Host | Linux, Network, Windows, macOS | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0022 | Center for Threat-Informed Defense (CTID)
File: File Access |  | x-mitre-data-component--235b7491-2d2b-4617-9a52-3c0783680f71 | Opening a file, which makes the file contents available to the requestor (ex: Windows EID 4663) |  |  | 20 October 2021 |  | datacomponent | 1.0
File: File Creation |  | x-mitre-data-component--2b3bfe19-d59a-460d-93bb-2f546adc2d2c | Initial construction of a new file (ex: Sysmon EID 11) |  |  | 20 October 2021 |  | datacomponent | 1.0
File: File Deletion |  | x-mitre-data-component--e905dad2-00d6-477c-97e8-800427abd0e8 | Removal of a file (ex: Sysmon EID 23, macOS ESF EID ES_EVENT_TYPE_AUTH_UNLINK, or Linux commands auditd unlink, rename, rmdir, unlinked, or renameat rules) |  |  | 20 October 2021 |  | datacomponent | 1.0
File: File Metadata |  | x-mitre-data-component--639e87f3-acb6-448a-9645-258f20da4bc5 | Contextual data about a file, which may include information such as name, the content (ex: signature, headers, or data/media), user/owner, permissions, etc. |  |  | 20 October 2021 |  | datacomponent | 1.0
File: File Modification |  | x-mitre-data-component--84572de3-9583-4c73-aabd-06ea88123dd8 | Changes made to a file, or its access permissions and attributes, typically to alter the contents of the targeted file (ex: Windows EID 4670 or Sysmon EID 2) |  |  | 20 October 2021 |  | datacomponent | 1.0
Firmware | DS0001 | x-mitre-data-source--ca1cb239-ff6d-4f64-b9d7-41c8556a8b4f | Computer software that provides low-level control for the hardware and device(s) of a host, such as BIOS or UEFI/EFI | Host | Linux, Windows, macOS | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0001 | Center for Threat-Informed Defense (CTID)
Firmware: Firmware Modification |  | x-mitre-data-component--b9d031bb-d150-4fc6-8025-688201bf3ffd | Changes made to firmware, including its settings and/or data, such as MBR (Master Boot Record) and VBR (Volume Boot Record) |  |  | 20 October 2021 |  | datacomponent | 1.0
Logon Session | DS0028 | x-mitre-data-source--4358c631-e253-4557-86df-f687d0ef9891 | Logon occurring on a system or resource (local, domain, or cloud) to which a user/device is gaining access after successful authentication and authorization(Citation: Microsoft Audit Logon Events) | Cloud Control Plane, Host, Network | Azure AD, Google Workspace, IaaS, Linux, Office 365, SaaS, Windows, macOS | 20 October 2021 |  | datasource | 1.1 | https://attack.mitre.org/datasources/DS0028 | Center for Threat-Informed Defense (CTID)
Logon Session: Logon Session Creation |  | x-mitre-data-component--9ce98c86-8d30-4043-ba54-0784d478d0b5 | Initial construction of a successful new user logon following an authentication attempt. (e.g. Windows EID 4624, /var/log/utmp, or /var/log/wmtp) |  |  | 20 October 2021 |  | datacomponent | 1.1
Logon Session: Logon Session Metadata |  | x-mitre-data-component--39b9db72-8b48-4595-a18d-db5bbba3091b | Contextual data about a logon session, such as username, logon type, access tokens (security context, user SIDs, logon identifiers, and logon SID), and any activity associated within it |  |  | 20 October 2021 |  | datacomponent | 1.0
Module | DS0011 | x-mitre-data-source--f424e4b4-a8a4-4c58-a4ae-4f53bfd08563 | Executable files consisting of one or more shared classes and interfaces, such as portable executable (PE) format binaries/dynamic link libraries (DLL), executable and linkable format (ELF) binaries/shared libraries, and Mach-O format binaries/shared libraries(Citation: Microsoft LoadLibrary)(Citation: Microsoft Module Class) | Host | Linux, Windows, macOS | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0011 | Center for Threat-Informed Defense (CTID)
Module: Module Load |  | x-mitre-data-component--c0a4a086-cc20-4e1e-b7cb-29d99dfa3fb1 | Attaching a module into the memory of a process/program, typically to access shared resources/features provided by the module (ex: Sysmon EID 7) |  |  | 20 October 2021 |  | datacomponent | 1.0
Network Share | DS0033 | x-mitre-data-source--ba27545a-9c32-47ea-ba6a-cce50f1b326e | A storage resource (typically a folder or drive) made available from one host to others using network protocols, such as Server Message Block (SMB) or Network File System (NFS)(Citation: Microsoft NFS Overview) | Host | Linux, Windows, macOS | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0033 | Center for Threat-Informed Defense (CTID)
Network Share: Network Share Access |  | x-mitre-data-component--f5468e67-51c7-4756-9b4f-65707708e7fa | Opening a network share, which makes the contents available to the requestor (ex: Windows EID 5140 or 5145) |  |  | 20 October 2021 |  | datacomponent | 1.0
Network Traffic | DS0029 | x-mitre-data-source--c000cd5c-bbb3-4606-af6f-6c6d9de0bbe3 | Data transmitted across a network (ex: Web, DNS, Mail, File, etc.), that is either summarized (ex: Netflow) and/or captured as raw data in an analyzable format (ex: PCAP) | Cloud Control Plane, Host, Network | Android, IaaS, Linux, Windows, iOS, macOS | 20 October 2021 |  | datasource | 1.1 | https://attack.mitre.org/datasources/DS0029 | Center for Threat-Informed Defense (CTID); ExtraHop
Network Traffic: Network Connection Creation |  | x-mitre-data-component--181a9f8c-c780-4f1f-91a8-edb770e904ba | Initial construction of a network connection, such as capturing socket information with a source/destination IP and port(s) (ex: Windows EID 5156, Sysmon EID 3, or Zeek conn.log) |  |  | 20 October 2021 |  | datacomponent | 1.1
Network Traffic: Network Traffic Content |  | x-mitre-data-component--3772e279-27d6-477a-9fe3-c6beb363594c | Logged network traffic data showing both protocol header and body values (ex: PCAP) |  |  | 20 October 2021 |  | datacomponent | 1.0
Network Traffic: Network Traffic Flow |  | x-mitre-data-component--a7f22107-02e5-4982-9067-6625d4a1765a | Summarized network packet data, with metrics, such as protocol headers and volume (ex: Netflow or Zeek http.log) |  |  | 20 October 2021 |  | datacomponent | 1.0
Operational Databases | DS0040 | x-mitre-data-source--1b8c9f31-ad35-4850-bf8c-80c565ad3552 | Operational databases contain information about the status of the operational process and associated devices, including any measurements, events, history, or alarms that have occurred | Host |  | 11 May 2022 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0040
Operational Databases: Device Alarm |  | x-mitre-data-component--9d56be63-3501-4dd3-bb5f-63c580833298 | This includes alarms associated with unexpected device functions, such as shutdowns, restarts, failures, or configuration changes |  |  | 11 May 2022 |  | datacomponent | 1.0
Operational Databases: Process History/Live Data |  | x-mitre-data-component--931b3fc6-ad68-42a8-9018-e98515eedc95 | This includes any data stores that maintain historical or real-time events and telemetry recorded from various sensors or devices |  |  | 11 May 2022 |  | datacomponent | 1.0
Operational Databases: Process/Event Alarm |  | x-mitre-data-component--4c12c1c8-bcef-4daf-8e5b-fca235f71d9e | This includes a list of any process alarms or alerts produced to indicate unusual or concerning activity within the operational process (e.g., increased temperature/pressure) |  |  | 11 May 2022 |  | datacomponent | 1.0
Process | DS0009 | x-mitre-data-source--e8b8ede7-337b-4c0c-8c32-5c7872c1ee22 | Instances of computer programs that are being executed by at least one thread. Processes have memory space for process executables, loaded modules (DLLs or shared libraries), and allocated memory regions containing everything from user input to application-specific data structures(Citation: Microsoft Processes and Threads) | Host | Android, Linux, Windows, iOS, macOS | 20 October 2021 |  | datasource | 1.1 | https://attack.mitre.org/datasources/DS0009 | Center for Threat-Informed Defense (CTID)
Process: OS API Execution |  | x-mitre-data-component--9bde2f9d-a695-4344-bfac-f2dce13d121e | Operating system function/method calls executed by a process |  |  | 20 October 2021 |  | datacomponent | 1.0
Process: Process Creation |  | x-mitre-data-component--3d20385b-24ef-40e1-9f56-f39750379077 | The initial construction of an executable managed by the OS, that may involve one or more tasks or threads. (e.g. Win EID 4688, Sysmon EID 1, cmd.exe > net use, etc.) |  |  | 20 October 2021 |  | datacomponent | 1.1
Process: Process Metadata |  | x-mitre-data-component--ee575f4a-2d4f-48f6-b18b-89067760adc1 | Contextual data about a running process, which may include information such as environment variables, image name, user/owner, etc. |  |  | 20 October 2021 |  | datacomponent | 1.0
Process: Process Termination |  | x-mitre-data-component--61f1d40e-f3d0-4cc6-aa2d-937b6204194f | Exit of a running process (ex: Sysmon EID 5 or Windows EID 4689) |  |  | 20 October 2021 |  | datacomponent | 1.0
Scheduled Job | DS0003 | x-mitre-data-source--c9ddfb51-eb45-4e22-b614-44ac1caa7883 | Automated tasks that can be executed at a specific time or on a recurring schedule running in the background (ex: Cron daemon, task scheduler, BITS)(Citation: Microsoft Tasks) | Container, Host | Containers, Linux, Windows, macOS | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0003 | Center for Threat-Informed Defense (CTID)
Scheduled Job: Scheduled Job Creation |  | x-mitre-data-component--f42df6f0-6395-4f0c-9376-525a031f00c3 | Initial construction of a new scheduled job (ex: Windows EID 4698 or /var/log cron logs) |  |  | 20 October 2021 |  | datacomponent | 1.0
Scheduled Job: Scheduled Job Metadata |  | x-mitre-data-component--7b375092-3a61-448d-900a-77c9a4bde4dc | Contextual data about a scheduled job, which may include information such as name, timing, command(s), etc. |  |  | 20 October 2021 |  | datacomponent | 1.0
Scheduled Job: Scheduled Job Modification |  | x-mitre-data-component--faa34cf6-cf32-4dc9-bd6a-8f7a606ff65b | Changes made to a scheduled job, such as modifications to the execution launch (ex: Windows EID 4702 or /var/log cron logs) |  |  | 20 October 2021 |  | datacomponent | 1.0
Script | DS0012 | x-mitre-data-source--12c1e727-7fa4-49b6-af81-366ed2ce231e | A file or stream containing a list of commands, allowing them to be launched in sequence(Citation: Microsoft PowerShell Logging)(Citation: FireEye PowerShell Logging)(Citation: Microsoft AMSI) | Host | Windows | 20 October 2021 |  | datasource | 1.1 | https://attack.mitre.org/datasources/DS0012 | Center for Threat-Informed Defense (CTID)
Script: Script Execution |  | x-mitre-data-component--9f387817-df83-432a-b56b-a8fb7f71eedd | The execution of a text file that contains code via the interpreter (e.g. Powershell, WMI, Windows EID 4104, etc.) |  |  | 20 October 2021 |  | datacomponent | 1.1
Service | DS0019 | x-mitre-data-source--d710099e-df94-4be4-bf85-cabd30e912bb | A computer process that is configured to execute continuously in the background and perform system tasks, in some cases before any user has logged in(Citation: Microsoft Services)(Citation: Linux Services Run Levels) | Host | Linux, Windows, macOS | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0019 | Center for Threat-Informed Defense (CTID)
Service: Service Creation |  | x-mitre-data-component--5297a638-1382-4f0c-8472-0d21830bf705 | Initial construction of a new service/daemon (ex: Windows EID 4697 or /var/log daemon logs) |  |  | 20 October 2021 |  | datacomponent | 1.0
Service: Service Metadata |  | x-mitre-data-component--74fa567d-bc90-425c-8a41-3c703abb221c | Contextual data about a service/daemon, which may include information such as name, service executable, start type, etc. |  |  | 20 October 2021 |  | datacomponent | 1.0
Service: Service Modification |  | x-mitre-data-component--66531bc6-a509-4868-8314-4d599e91d222 | Changes made to a service/daemon, such as changes to name, description, and/or start type (ex: Windows EID 7040 or /var/log daemon logs) |  |  | 20 October 2021 |  | datacomponent | 1.0
User Account | DS0002 | x-mitre-data-source--0b4f86ed-f4ab-46a3-8ed1-175be1974da6 | A profile representing a user, device, service, or application used to authenticate and access resources | Cloud Control Plane, Container, Host | Azure AD, Containers, Google Workspace, IaaS, Linux, Office 365, SaaS, Windows, macOS | 20 October 2021 |  | datasource | 1.1 | https://attack.mitre.org/datasources/DS0002 | Center for Threat-Informed Defense (CTID)
User Account: User Account Authentication |  | x-mitre-data-component--a953ca55-921a-44f7-9b8d-3d40141aa17e | An attempt by a user to gain access to a network or computing resource, often by providing credentials (ex: Windows EID 4776 or /var/log/auth.log) |  |  | 20 October 2021 |  | datacomponent | 1.1
Windows Registry | DS0024 | x-mitre-data-source--0f42a24c-e035-4f93-a91c-5f7076bd8da0 | A Windows OS hierarchical database that stores much of the information and settings for software programs, hardware devices, user preferences, and operating-system configurations(Citation: Microsoft Registry) | Host | Windows | 20 October 2021 |  | datasource | 1.0 | https://attack.mitre.org/datasources/DS0024
Windows Registry: Windows Registry Key Deletion |  | x-mitre-data-component--1177a4c5-31c8-400c-8544-9071166afa0e | Removal of a Registry Key (ex: Windows EID 4658 or Sysmon EID 12) |  |  | 20 October 2021 |  | datacomponent | 1.0
Windows Registry: Windows Registry Key Modification |  | x-mitre-data-component--da85d358-741a-410d-9433-20d6269a6170 | Changes made to a Registry Key and/or Key value (ex: Windows EID 4657 or Sysmon EID 13¦14) |  |  | 20 October 2021 |  | datacomponent | 1.0

## citations
reference | citation | url
A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004 | A G Foord, W G Gulland, C R Howard, T Kellacher, W H Smith 2004 APPLYING THE LATEST STANDARD FOR FUNCTIONAL SAFETY IEC 61511 Retrieved. 2020/09/17 | https://www.icheme.org/media/9906/xviii-paper-23.pdf
ACSC Email Spoofing | Australian Cyber Security Centre. (2012, December). Mitigating Spoofed Emails Using Sender Policy Framework. Retrieved October 19, 2020. | https://www.cyber.gov.au/sites/default/files/2019-03/spoof_email_sender_policy_framework.pdf
APT34 | This group was previously tracked under two distinct groups, APT34 and OilRig, but was combined due to additional reporting giving higher confidence about the overlap of the activity.(Citation: Unit 42 QUADAGENT July 2018)(Citation: FireEye APT34 Dec 2017)(Citation: Check Point APT34 April 2021)
Accenture Lyceum Targets November 2021 | Accenture. (2021, November 9). Who are latest targets of cyber group Lyceum?. Retrieved June 16, 2022. | https://www.accenture.com/us-en/blogs/cyber-defense/iran-based-lyceum-campaigns
Aditya K Sood July 2019 | Aditya K Sood 2019, July Discovering and fingerprinting BACnet devices Retrieved. 2020/09/25 | https://www.helpnetsecurity.com/2019/07/10/bacnet-devices/
Alexander Bolshev March 2014 | Alexander Bolshev 2014, March 11 S4x14: HART As An Attack Vector Retrieved. 2020/01/05 | https://www.slideshare.net/dgpeters/17-bolshev-1-13
Alexander Bolshev, Gleb Cherbov July 2014 | Alexander Bolshev, Gleb Cherbov 2014, July 08 ICSCorsair: How I will PWN your ERP through 4-20 mA current loop Retrieved. 2020/01/05 | https://www.blackhat.com/docs/us-14/materials/us-14-Bolshev-ICSCorsair-How-I-Will-PWN-Your-ERP-Through-4-20mA-Current-Loop-WP.pdf
Andy Greenberg June 2017 | Andy Greenberg. (2017, June 28). How an Entire Nation Became Russia's Test Lab for Cyberwar. Retrieved September 27, 2023. | https://www.wired.com/story/russian-hackers-attack-ukraine/
Andy Greenburg June 2019 | Andy Greenburg 2019, June 20 Iranian Hackers Launch a New US-Targeted Campaign as Tensions Mount Retrieved. 2020/01/03 | https://www.wired.com/story/iran-hackers-us-phishing-tensions/
Antiquated Mac Malware | Thomas Reed. (2017, January 18). New Mac backdoor using antiquated code. Retrieved July 5, 2017. | https://blog.malwarebytes.com/threat-analysis/2017/01/new-mac-backdoor-using-antiquated-code/
Anton Cherepanov | Anton Cherepanov BlackEnergy by the SSHBearDoor: attacks against Ukrainian news media and electric industry Retrieved. 2019/10/29 | https://www.welivesecurity.com/2016/01/03/blackenergy-sshbeardoor-details-2015-attacks-ukrainian-news-media-electric-industry/
Anton Cherepanov, ESET June 2017 | Anton Cherepanov, ESET 2017, June 12 Win32/Industroyer: A new threat for industrial control systems Retrieved. 2017/09/15 | https://www.welivesecurity.com/wp-content/uploads/2017/06/Win32_Industroyer.pdf
Atlassian Confluence Logging | Atlassian. (2018, January 9). How to Enable User Access Logging. Retrieved April 4, 2018. | https://confluence.atlassian.com/confkb/how-to-enable-user-access-logging-182943.html
Audit OSX | Gagliardi, R. (n.d.). Audit in a OS X System. Retrieved September 23, 2021. | https://www.scip.ch/en/?labs.20150108
BBC April 2016 | BBC 2016, April 28 German nuclear plant hit by computer viruses Retrieved. 2019/10/14 | https://www.bbc.com/news/technology-36158606
BSI State of IT Security 2014 | Bundesamt fr Sicherheit in der Informationstechnik (BSI) (German Federal Office for Information Security) 2014 Die Lage der IT-Sicherheit in Deutschland 2014 (The State of IT Security in Germany) Retrieved. 2019/10/30 | https://www.bsi.bund.de/SharedDocs/Downloads/EN/BSI/Publications/Securitysituation/IT-Security-Situation-in-Germany-2014.pdf?__blob=publicationFile&v=3
Basnight, Zachry, et al. | Basnight, Zachry, et al. 2013 Retrieved. 2017/10/17 | http://www.sciencedirect.com/science/article/pii/S1874548213000231
Bastille April 2017 | Bastille 2017, April 17 Dallas Siren Attack Retrieved. 2020/11/06 | https://www.bastille.net/blogs/2017/4/17/dallas-siren-attack
Beckhoff | Beckhoff TwinCAT 3 Source Control: Project Files Retrieved. 2019/11/21 | https://infosys.beckhoff.com/english.php?content=../content/1033/tc3_sourcecontrol/18014398915785483.html&id=
Ben Hunter and Fred Gutierrez July 2020 | Ben Hunter and Fred Gutierrez 2020, July 01 EKANS Ransomware Targeting OT ICS Systems Retrieved. 2021/04/12 | https://www.fortinet.com/blog/threat-research/ekans-ransomware-targeting-ot-ics-systems
Benjamin Freed March 2019 | Benjamin Freed 2019, March 13 Tornado sirens in Dallas suburbs deactivated after being hacked and set off Retrieved. 2020/11/06 | https://statescoop.com/tornado-sirens-in-dallas-suburbs-deactivated-after-being-hacked-and-set-off/
Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer December 2017 | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer 2017, December 14 Attackers Deploy New ICS Attack Framework TRITON and Cause Operational Disruption to Critical Infrastructure Retrieved. 2018/01/12 | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
Bleeping Computer - Ryuk WoL | Abrams, L. (2021, January 14). Ryuk Ransomware Uses Wake-on-Lan To Encrypt Offline Devices. Retrieved February 11, 2021. | https://www.bleepingcomputer.com/news/security/ryuk-ransomware-uses-wake-on-lan-to-encrypt-offline-devices/
Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011 | Bonnie Zhu, Anthony Joseph, Shankar Sastry 2011 A Taxonomy of Cyber Attacks on SCADA Systems Retrieved. 2018/01/12 | http://ieeexplore.ieee.org/stamp/stamp.jsp?tp=&arnumber=6142258
Booz Allen Hamilton | Booz Allen Hamilton When The Lights Went Out Retrieved. 2019/10/22 | https://www.boozallen.com/content/dam/boozallen/documents/2016/09/ukraine-report-when-the-lights-went-out.pdf
Brubaker-Incontroller | Nathan Brubaker, Keith Lunden, Ken Proska, Muhammad Umair, Daniel Kapellmann Zafra, Corey Hildebrandt, Rob Caldwell. (2022, April 13). INCONTROLLER: New State-Sponsored Cyber Attack Tools Target Multiple Industrial Control Systems. Retrieved September 28, 2022. | https://www.mandiant.com/resources/incontroller-state-sponsored-ics-tool
Bruce Schneier January 2008 | Bruce Schneier 2008, January 17 Hacking Polish Trams Retrieved. 2019/10/17 | https://www.schneier.com/blog/archives/2008/01/hacking_the_pol.html
CISA AA20-239A BeagleBoyz August 2020 | DHS/CISA. (2020, August 26). FASTCash 2.0: North Korea's BeagleBoyz Robbing Banks. Retrieved September 29, 2021. | https://us-cert.cisa.gov/ncas/alerts/aa20-239a
CISA AA20-296A Berserk Bear December 2020 | CISA. (2020, December 1). Russian State-Sponsored Advanced Persistent Threat Actor Compromises U.S. Government Targets. Retrieved December 9, 2021. | https://www.cisa.gov/uscert/ncas/alerts/aa20-296a#revisions
CISA AA21-201A Pipeline Intrusion July 2021 | Department of Justice (DOJ), DHS Cybersecurity & Infrastructure Security Agency (CISA) 2021, July 20 Chinese Gas Pipeline Intrusion Campaign, 2011 to 2013 Retrieved. 2021/10/08 | https://us-cert.cisa.gov/sites/default/files/publications/AA21-201A_Chinese_Gas_Pipeline_Intrusion_Campaign_2011_to_2013%20(1).pdf
CISA AA23-335A IRGC-Affiliated December 2023 | DHS/CISA. (2023, December 1). IRGC-Affiliated Cyber Actors Exploit PLCs in Multiple Sectors, Including U.S. Water and Wastewater Systems Facilities. Retrieved March 25, 2024. | https://www.cisa.gov/news-events/cybersecurity-advisories/aa23-335a
CISA ICS Advisory ICSA-10-272-01 | CISA. (2010, September 10). ICS Advisory (ICSA-10-272-01). Retrieved December 7, 2020. | https://us-cert.cisa.gov/ics/advisories/ICSA-10-272-01
CISA June 2013 | CISA 2013, June Risks of Default Passwords on the Internet Retrieved. 2020/09/25 | https://us-cert.cisa.gov/ncas/alerts/TA13-175A
CISA March 2010 | CISA 2010, March 11 https://us-cert.cisa.gov/ncas/tips/ST05-003 Retrieved. 2020/09/25 | https://us-cert.cisa.gov/ncas/tips/ST05-003
CISA Unitronics November 2023 | DHS/CISA. (2023, November 28). Exploitation of Unitronics PLCs used in Water and Wastewater Systems. Retrieved March 25, 2024. | https://www.cisa.gov/news-events/alerts/2023/11/28/exploitation-unitronics-plcs-used-water-and-wastewater-systems
CISA-AA22-103A | DHS/CISA. (2022, May 25). Alert (AA22-103A) APT Cyber Tools Targeting ICS/SCADA Devices. Retrieved September 28, 2022. | https://www.cisa.gov/uscert/ncas/alerts/aa22-103a
Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. April 2018 | Candell, R., Hany, M., Lee, K. B., Liu,Y., Quimby, J., Remley, K. 2018, April Guide to Industrial Wireless Systems Deployments Retrieved. 2020/12/01 | https://nvlpubs.nist.gov/nistpubs/ams/NIST.AMS.300-4.pdf
CarbonBlack LockerGoga 2019 | CarbonBlack Threat Analysis Unit. (2019, March 22). TAU Threat Intelligence Notification – LockerGoga Ransomware. Retrieved April 16, 2019. | https://www.carbonblack.com/2019/03/22/tau-threat-intelligence-notification-lockergoga-ransomware/
Carl Hurd March 2019 | Carl Hurd 2019, March 26 VPNFilter Deep Dive Retrieved. 2019/03/28 | https://www.youtube.com/watch?v=yuZazP22rpI
Catalin Cimpanu April 2016 | Catalin Cimpanu 2016, April 26 Malware Shuts Down German Nuclear Power Plant on Chernobyl's 30th Anniversary Retrieved. 2019/10/14 | https://news.softpedia.com/news/on-chernobyl-s-30th-anniversary-malware-shuts-down-german-nuclear-power-plant-503429.shtml
Centre for the Protection of National Infrastructure February 2005 | Centre for the Protection of National Infrastructure 2005, February FIREWALL DEPLOYMENT FOR SCADA AND PROCESS CONTROL NETWORKS Retrieved. 2020/09/17 | https://www.energy.gov/sites/prod/files/Good%20Practices%20Guide%20for%20Firewall%20Deployment.pdf
Centre for the Protection of National Infrastructure November 2010 | Centre for the Protection of National Infrastructure 2010, November Configuring and Managing Remote Access for Industrial Control Systems Retrieved. 2020/09/25 | https://us-cert.cisa.gov/sites/default/files/recommended_practices/RP_Managing_Remote_Access_S508NC.pdf
Charles McLellan March 2016 | Charles McLellan. (2016, March 4). How hackers attacked Ukraine's power grid: Implications for Industrial IoT security. Retrieved September 27, 2023. | https://www.zdnet.com/article/how-hackers-attacked-ukraines-power-grid-implications-for-industrial-iot-security/
Check Point APT34 April 2021 | Check Point. (2021, April 8). Iran’s APT34 Returns with an Updated Arsenal. Retrieved May 5, 2021. | https://research.checkpoint.com/2021/irans-apt34-returns-with-an-updated-arsenal/
Chris Bing May 2018 | Chris Bing 2018, May 24 Trisis masterminds have expanded operations to target U.S. industrial firms Retrieved. 2020/01/03 | https://www.cyberscoop.com/xenotime-ics-cyber-attacks-trisis-dragos/
Christoph Steitz, Eric Auchard April 2016 | Christoph Steitz, Eric Auchard 2016, April 26 German nuclear plant infected with computer viruses, operator says Retrieved. 2019/10/14 | https://www.reuters.com/article/us-nuclearpower-cyber-germany/german-nuclear-plant-infected-with-computer-viruses-operator-says-idUSKCN0XN2OS
ClearSky OilRig Jan 2017 | ClearSky Cybersecurity. (2017, January 5). Iranian Threat Agent OilRig Delivers Digitally Signed Malware, Impersonates University of Oxford. Retrieved May 3, 2017. | http://www.clearskysec.com/oilrig/
ClearSky Siamesekitten August 2021 | ClearSky Cyber Security . (2021, August). New Iranian Espionage Campaign By “Siamesekitten” - Lyceum. Retrieved June 6, 2022. | https://www.clearskysec.com/siamesekitten/
Colin Gray | Colin Gray D. Parsons and D. Wylie 2019, September Practical Industrial Control System (ICS) Cybersecurity: IT and OT Have Converged Discover and Defend Your Assets Retrieved. 2020/09/25 How SDN Can Improve Cybersecurity in OT Networks Retrieved. 2020/09/25 | https://cdn.selinc.com/assets/Literature/Publications/Technical%20Papers/6891_HowSDN_CG_20180720_Web2.pdf?v=20190312-231901
Colonial Pipeline Company May 2021 | Colonial Pipeline Company 2021, May Media Statement Update: Colonial Pipeline System Disruption Retrieved. 2021/10/08 | https://www.colpipe.com/news/press-releases/media-statement-colonial-pipeline-system-disruption
Common Weakness Enumeration January 2019 | Common Weakness Enumeration 2019, January 03 CWE-400: Uncontrolled Resource Consumption Retrieved. 2019/03/14 | http://cwe.mitre.org/data/definitions/400.html
Conficker Nuclear Power Plant | Cimpanu, C. (2016, April 26). Malware Shuts Down German Nuclear Power Plant on Chernobyl's 30th Anniversary. Retrieved February 18, 2021. | https://news.softpedia.com/news/on-chernobyl-s-30th-anniversary-malware-shuts-down-german-nuclear-power-plant-503429.shtml
Confluence Linux Command Line | Confluence Support. (2021, September 8). How to enable command line audit logging in linux. Retrieved September 23, 2021. | https://confluence.atlassian.com/confkb/how-to-enable-command-line-audit-logging-in-linux-956166545.html
Confluence Logs | Confluence Support. (2021, April 22). Working with Confluence Logs. Retrieved September 23, 2021. | https://confluence.atlassian.com/doc/working-with-confluence-logs-108364721.html
Control Global May 2019 | Control Global 2019, May 29 Yokogawa announcement warns of counterfeit transmitters Retrieved. 2021/04/09 | https://www.controlglobal.com/industrynews/2019/yokogawa-announcement-warns-of-counterfeit-transmitters/
CopyFromScreen .NET | Microsoft. (n.d.). Graphics.CopyFromScreen Method. Retrieved March 24, 2020. | https://docs.microsoft.com/en-us/dotnet/api/system.drawing.graphics.copyfromscreen?view=netframework-4.8
Corero | Corero Industrial Control System (ICS) Security Retrieved. 2019/11/04 | https://www.corero.com/resources/files/whitepapers/cns_whitepaper_ics.pdf
CrowdStrike Carbon Spider August 2021 | Loui, E. and Reynolds, J. (2021, August 30). CARBON SPIDER Embraces Big Game Hunting, Part 1. Retrieved September 20, 2021. | https://www.crowdstrike.com/blog/carbon-spider-embraces-big-game-hunting-part-1/
CrowdStrike Evolution of Pinchy Spider July 2021 | Meyers, Adam. (2021, July 6). The Evolution of PINCHY SPIDER from GandCrab to REvil. Retrieved March 28, 2023. | https://www.crowdstrike.com/blog/the-evolution-of-revil-ransomware-and-pinchy-spider/
CrowdStrike GTR 2021 June 2021 | CrowdStrike. (2021, June 7). CrowdStrike 2021 Global Threat Report. Retrieved September 29, 2021. | https://go.crowdstrike.com/rs/281-OBQ-266/images/Report2021GTR.pdf
CrowdStrike Grim Spider May 2019 | John, E. and Carvey, H. (2019, May 30). Unraveling the Spiderweb: Timelining ATT&CK Artifacts Used by GRIM SPIDER. Retrieved May 12, 2020. | https://www.crowdstrike.com/blog/timelining-grim-spiders-big-game-hunting-tactics/
CrowdStrike Labyrinth Chollima Feb 2022 | CrowdStrike. (2022, February 1). CrowdStrike Adversary Labyrinth Chollima. Retrieved February 1, 2022. | https://web.archive.org/web/20210723190317/https://adversary.crowdstrike.com/en-US/adversary/labyrinth-chollima/
CrowdStrike Ryuk January 2019 | Hanel, A. (2019, January 10). Big Game Hunting with Ryuk: Another Lucrative Targeted Ransomware. Retrieved May 12, 2020. | https://www.crowdstrike.com/blog/big-game-hunting-with-ryuk-another-lucrative-targeted-ransomware/
CrowdStrike Stardust Chollima Profile April 2018 | Meyers, Adam. (2018, April 6). Meet CrowdStrike’s Adversary of the Month for April: STARDUST CHOLLIMA. Retrieved September 29, 2021. | https://www.crowdstrike.com/blog/meet-crowdstrikes-adversary-of-the-month-for-april-stardust-chollima/
CrowdStrike VOODOO BEAR | Meyers, A. (2018, January 19). Meet CrowdStrike’s Adversary of the Month for January: VOODOO BEAR. Retrieved May 22, 2018. | https://www.crowdstrike.com/blog/meet-crowdstrikes-adversary-of-the-month-for-january-voodoo-bear/
CrowdStrike Wizard Spider October 2020 | Podlosky, A., Hanel, A. et al. (2020, October 16). WIZARD SPIDER Update: Resilient, Reactive and Resolute. Retrieved June 15, 2021. | https://www.crowdstrike.com/blog/wizard-spider-adversary-update/
Crowdstrike Global Threat Report Feb 2018 | CrowdStrike. (2018, February 26). CrowdStrike 2018 Global Threat Report. Retrieved October 10, 2018. | https://crowdstrike.lookbookhq.com/global-threat-report-2018-web/cs-2018-global-threat-report
Crowdstrike Helix Kitten Nov 2018 | Meyers, A. (2018, November 27). Meet CrowdStrike’s Adversary of the Month for November: HELIX KITTEN. Retrieved December 18, 2018. | https://www.crowdstrike.com/blog/meet-crowdstrikes-adversary-of-the-month-for-november-helix-kitten/
Crysys Skywiper | sKyWIper Analysis Team. (2012, May 31). sKyWIper (a.k.a. Flame a.k.a. Flamer): A complex malware for targeted attacks. Retrieved September 6, 2018. | https://www.crysys.hu/publications/files/skywiper.pdf
Cybersecurity & Infrastructure Security Agency March 2018 | Cybersecurity & Infrastructure Security Agency 2018, March 15 Alert (TA18-074A) Russian Government Cyber Activity Targeting Energy and Other Critical Infrastructure Sectors Retrieved. 2019/10/11 | https://us-cert.cisa.gov/ncas/alerts/TA18-074A
Cylance Sodinokibi July 2019 | Cylance. (2019, July 3). hreat Spotlight: Sodinokibi Ransomware. Retrieved August 4, 2020. | https://threatvector.cylance.com/en_us/home/threat-spotlight-sodinokibi-ransomware.html
D. Parsons and D. Wylie September 2019 | D. Parsons and D. Wylie 2019, September Practical Industrial Control System (ICS) Cybersecurity: IT and OT Have Converged Discover and Defend Your Assets Retrieved. 2020/09/25 | https://www.csiac.org/journal-article/practical-industrial-control-system-ics-cybersecurity-it-and-ot-have-converged-discover-and-defend-your-assets/
DFIR Ryuk 2 Hour Speed Run November 2020 | The DFIR Report. (2020, November 5). Ryuk Speed Run, 2 Hours to Ransom. Retrieved November 6, 2020. | https://thedfirreport.com/2020/11/05/ryuk-speed-run-2-hours-to-ransom/
DFIR Ryuk in 5 Hours October 2020 | The DFIR Report. (2020, October 18). Ryuk in 5 Hours. Retrieved October 19, 2020. | https://thedfirreport.com/2020/10/18/ryuk-in-5-hours/
DFIR Ryuk's Return October 2020 | The DFIR Report. (2020, October 8). Ryuk’s Return. Retrieved October 9, 2020. | https://thedfirreport.com/2020/10/08/ryuks-return/
DHS National Urban Security Technology Laboratory April 2019 | DHS National Urban Security Technology Laboratory 2019, April Radio Frequency Detection, Spectrum Analysis, and Direction Finding Equipment Retrieved. 2020/09/17 | https://www.dhs.gov/sites/default/files/saver-msr-rf-detection_cod-508_10july2019.pdf
DHS CISA February 2019 | DHS CISA 2019, February 27 MAR-17-352-01 HatManSafety System Targeted Malware (Update B) Retrieved. 2019/03/08 | https://ics-cert.us-cert.gov/sites/default/files/documents/MAR-17-352-01%20HatMan%20-%20Safety%20System%20Targeted%20Malware%20%28Update%20B%29.pdf
DHS/CISA Ransomware Targeting Healthcare October 2020 | DHS/CISA. (2020, October 28). Ransomware Activity Targeting the Healthcare and Public Health Sector. Retrieved October 28, 2020. | https://us-cert.cisa.gov/ncas/alerts/aa20-302a
DOJ North Korea Indictment Feb 2021 | Department of Justice. (2021, February 17). Three North Korean Military Hackers Indicted in Wide-Ranging Scheme to Commit Cyberattacks and Financial Crimes Across the Globe. Retrieved June 9, 2021. | https://www.justice.gov/opa/pr/three-north-korean-military-hackers-indicted-wide-ranging-scheme-commit-cyberattacks-and
DOJ Russia Targeting Critical Infrastructure March 2022 | Department of Justice. (2022, March 24). Four Russian Government Employees Charged in Two Historical Hacking Campaigns Targeting Critical Infrastructure Worldwide. Retrieved April 5, 2022. | https://www.justice.gov/opa/pr/four-russian-government-employees-charged-two-historical-hacking-campaigns-targeting-critical
Daavid Hentunen, Antti Tikkanen June 2014 | Daavid Hentunen, Antti Tikkanen 2014, June 23 Havex Hunts For ICS/SCADA Systems Retrieved. 2019/04/01 | https://www.f-secure.com/weblog/archives/00002718.html
Dan Goodin March 2017 | Dan Goodin 2017, March Virtual machine escape fetches $105,000 at Pwn2Own hacking contest Retrieved. 2020/09/25 | https://arstechnica.com/information-technology/2017/03/hack-that-escapes-vm-by-exploiting-edge-browser-fetches-105000-at-pwn2own/
Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly July 2020 | Daniel Kapellmann Zafra, Keith Lunden, Nathan Brubaker, Jeremy Kennelly 2020, July 15 Ransomware Against the Machine: How Adversaries are Learning to Disrupt Industrial Production by Targeting IT and OT Retrieved. 2021/04/12 | https://www.fireeye.com/blog/threat-research/2020/02/ransomware-against-machine-learning-to-disrupt-industrial-production.html
Daniel Oakley, Travis Smith, Tripwire | Daniel Oakley, Travis Smith, Tripwire Retrieved. 2018/05/30 | https://attack.mitre.org/wiki/Technique/T1133
Daniel Peck, Dale Peterson January 2009 | Daniel Peck, Dale Peterson 2009, January 28 Leveraging Ethernet Card Vulnerabilities in Field Devices Retrieved. 2017/12/19 | https://www.researchgate.net/publication/228849043_Leveraging_ethernet_card_vulnerabilities_in_field_devices
Danny Yadron December 2015 | Danny Yadron 2015, December 20 Iranian Hackers Infiltrated New York Dam in 2013 Retrieved. 2019/11/07 | https://www.wsj.com/articles/iranian-hackers-infiltrated-new-york-dam-in-2013-1450662559
Dark Reading Staff April 2016 | Dark Reading Staff 2016, April 28 German Nuclear Power Plant Infected With Malware Retrieved. 2019/10/14 | https://www.darkreading.com/endpoint/german-nuclear-power-plant-infected-with-malware/d/d-id/1325298
Davey Winder June 2020 | Davey Winder 2020, June 10 Honda Hacked: Japanese Car Giant Confirms Cyber Attack On Global Operations Retrieved. 2021/04/12 | https://www.forbes.com/sites/daveywinder/2020/06/10/honda-hacked-japanese-car-giant-confirms-cyber-attack-on-global-operations-snake-ransomware/?sh=2725c35753ad
David Voreacos, Katherine Chinglinsky, Riley Griffin December 2019 | David Voreacos, Katherine Chinglinsky, Riley Griffin 2019, December 03 Merck Cyberattacks $1.3 Billion Question: Was It an Act of War? Retrieved. 2019/12/06 | https://www.bloomberg.com/news/features/2019-12-03/merck-cyberattack-s-1-3-billion-question-was-it-an-act-of-war
Defense Advanced Research Projects Agency | Defense Advanced Research Projects Agency National Institute of Standards and Technology 2013, April Security and Privacy Controls for Federal Information Systems and Organizations Retrieved. 2020/09/17 Rapid Attack Detection, Isolation and Characterization Systems (RADICS) Retrieved. 2020/09/17 | https://www.darpa.mil/program/rapid-attack-detection-isolation-and-characterization-systems
Dennis L. Sloatman September 2016 | Dennis L. Sloatman 2016, September 16 Understanding PLC Programming Methods and the Tag Database System Retrieved. 2017/12/19 | https://www.radioworld.com/industry/understanding-plc-programming-methods-and-the-tag-database-system
Department of Homeland Security October 2009 | Department of Homeland Security 2009, October Developing an Industrial Control Systems Cybersecurity Incident Response Capability Retrieved. 2020/09/17 | https://us-cert.cisa.gov/sites/default/files/recommended_practices/final-RP_ics_cybersecurity_incident_response_100609.pdf
Department of Homeland Security September 2016 | Department of Homeland Security 2016, September Retrieved. 2020/09/25 | https://us-cert.cisa.gov/sites/default/files/recommended_practices/NCCIC_ICS-CERT_Defense_in_Depth_2016_S508C.pdf
Dr. Kelvin T. Erickson December 2010 | Dr. Kelvin T. Erickson 2010, December Programmable logic controller hardware Retrieved. 2018/03/29 | https://www.isa.org/standards-and-publications/isa-publications/intech/2010/december/programmable-logic-controller-hardware/
Dragos | Dragos Allanite Retrieved. 2019/10/27 | https://dragos.com/resource/allanite/
Dragos Crashoverride 2017 | Dragos Inc.. (2017, June 13). CRASHOVERRIDE Analysis of the Threat to Electric Grid Operations. Retrieved December 18, 2020. | https://dragos.com/blog/crashoverride/CrashOverride-01.pdf
Dragos Crashoverride 2018 | Joe Slowik. (2018, October 12). Anatomy of an Attack: Detecting and Defeating CRASHOVERRIDE. Retrieved December 18, 2020. | https://www.dragos.com/wp-content/uploads/CRASHOVERRIDE2018.pdf
Dragos DYMALLOY | Dragos. (n.d.). DYMALLOY. Retrieved August 20, 2020. | https://www.dragos.com/threat/dymalloy/
Dragos December 2017 | Dragos 2017, December 13 TRISIS Malware Analysis of Safety System Targeted Malware Retrieved. 2018/01/12 | https://dragos.com/blog/trisis/TRISIS-01.pdf
Dragos EKANS | Dragos. (2020, February 3). EKANS Ransomware and ICS Operations. Retrieved February 9, 2021. | https://www.dragos.com/blog/industry-news/ekans-ransomware-and-ics-operations/
Dragos ELECTRUM | Dragos. (2017, January 1). ELECTRUM Threat Profile. Retrieved June 10, 2020. | https://www.dragos.com/resource/electrum/
Dragos Hexane | Dragos. (n.d.). Hexane. Retrieved October 27, 2019. | https://dragos.com/resource/hexane/
Dragos IT ICS Ransomware | Slowik, J.. (2019, April 10). Implications of IT Ransomware for ICS Environments. Retrieved January 28, 2021. | https://www.dragos.com/blog/industry-news/implications-of-it-ransomware-for-ics-environments/
Dragos Inc. June 2017 | Dragos Inc. 2017, June 13 Industroyer - Dragos - 201706: Analysis of the Threat to Electic Grid Operations Retrieved. 2017/09/18 | https://dragos.com/blog/crashoverride/CrashOverride-01.pdf
Dragos October 2018 | Dragos 2018, October 12 Anatomy of an Attack: Detecting and Defeating CRASHOVERRIDE Retrieved. 2019/10/14 | https://dragos.com/wp-content/uploads/CRASHOVERRIDE2018.pdf
Dragos Threat Intelligence August 2019 | Dragos Threat Intelligence 2019, August Global Oil and Gas Cyber Threat Perspective Retrieved. 2020/01/03 | https://dragos.com/wp-content/uploads/Dragos-Oil-and-Gas-Threat-Perspective-2019.pdf
Dragos Threat Intelligence February 2020 | Dragos Threat Intelligence 2020, February 03 EKANS Ransomware and ICS Operations Retrieved. 2021/04/12 | https://www.dragos.com/blog/industry-news/ekans-ransomware-and-ics-operations/
Dragos Xenotime 2018 | Dragos, Inc.. (n.d.). Xenotime. Retrieved April 16, 2019. | https://dragos.com/resource/xenotime/
Dragos-Pipedream | DRAGOS. (2022, April 13). Pipedream: Chernovite’s Emerging Malware Targeting Industrial Control Systems. Retrieved September 28, 2022. | https://hub.dragos.com/hubfs/116-Whitepapers/Dragos_ChernoviteWP_v2b.pdf?hsLang=en
Dragos-Sandworm-Ukraine-2022 | Dragos, Inc.. (2023, December 11). ELECTRUM Targeted Ukrainian Electric Entity Using Custom Tools and CaddyWiper Malware, October 2022. Retrieved March 28, 2024. | https://www.dragos.com/blog/new-details-electrum-ukraine-electric-sector-compromise-2022/
Dwight Anderson 2014 | Dwight Anderson 2014 Protect Critical Infrastructure Systems With Whitelisting Retrieved. 2020/09/25 | https://www.sans.org/reading-room/whitepapers/ICS/protect-critical-infrastructure-systems-whitelisting-35312
ESEST Black Energy Jan 2016 | Cherepanov, A.. (2016, January 3). BlackEnergy by the SSHBearDoor: attacks against Ukrainian news media and electric industry. Retrieved May 18, 2016. | http://www.welivesecurity.com/2016/01/03/blackenergy-sshbeardoor-details-2015-attacks-ukrainian-news-media-electric-industry/
ESET | ESET ACAD/Medre.A: 10000s of AutoCAD Designs Leaked in Suspected Industrial Espionage Retrieved. 2021/04/13 | https://www.welivesecurity.com/wp-content/uploads/200x/white-papers/ESET_ACAD_Medre_A_whitepaper.pdf
ESET April 2016 | ESET 2016, April 28 Malware found at a German nuclear power plant Retrieved. 2019/10/14 | https://www.welivesecurity.com/2016/04/28/malware-found-german-nuclear-power-plant/
ESET Bad Rabbit | M.Léveille, M-E.. (2017, October 24). Bad Rabbit: Not‑Petya is back with improved ransomware. Retrieved January 28, 2021. | https://www.welivesecurity.com/2017/10/24/bad-rabbit-not-petya-back/
ESET Industroyer | Anton Cherepanov. (2017, June 12). Win32/Industroyer: A new threat for industrial controls systems. Retrieved December 18, 2020. | https://www.welivesecurity.com/wp-content/uploads/2017/06/Win32_Industroyer.pdf
ESET Lazarus KillDisk April 2018 | Kálnai, P., Cherepanov A. (2018, April 03). Lazarus KillDisks Central American casino. Retrieved May 17, 2018. | https://www.welivesecurity.com/2018/04/03/lazarus-killdisk-central-american-casino/
ESET Research Whitepapers September 2018 | ESET Research Whitepapers 2018, September LOJAX First UEFI rootkit found in the wild, courtesy of the Sednit group Retrieved. 2020/09/25 | https://www.welivesecurity.com/wp-content/uploads/2018/09/ESET-LoJax.pdf
ESET Stuxnet Under the Microscope | Matrosov, A., Rodionov, E., Harley, D., Malcho, J.. (n.d.). Stuxnet Under the Microscope. Retrieved December 7, 2020. | https://www.esetnod32.ru/company/viruslab/analytics/doc/Stuxnet_Under_the_Microscope.pdf
ESET Telebots June 2017 | Cherepanov, A.. (2017, June 30). TeleBots are back: Supply chain attacks against Ukraine. Retrieved June 11, 2020. | https://www.welivesecurity.com/2017/06/30/telebots-back-supply-chain-attacks-against-ukraine/
Eduard Kovacs March 2018 | Eduard Kovacs 2018, March 1 Five Threat Groups Target Industrial Systems: Dragos Retrieved. 2020/01/03 | https://www.securityweek.com/five-threat-groups-target-industrial-systems-dragos
Eduard Kovacs May 2018 | Eduard Kovacs 2018, May 21 Group linked to Shamoon attacks targeting ICS networks in Middle East and UK Retrieved. 2020/01/03 | https://www.cyberviser.com/2018/05/group-linked-to-shamoon-attacks-targeting-ics-networks-in-middle-east-and-uk/
Elastic - Koadiac Detection with EQL | Stepanic, D.. (2020, January 13). Embracing offensive tooling: Building detections against Koadic using EQL. Retrieved November 30, 2020. | https://www.elastic.co/blog/embracing-offensive-tooling-building-detections-against-koadic-using-eql
Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems March 2016 | Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems 2016, March 18 Analysis of the Cyber Attack on the Ukranian Power Grid: Defense Use Case Retrieved. 2018/03/27 | https://assets.contentstack.io/v3/assets/blt36c2e63521272fdc/blt6a77276749b76a40/607f235992f0063e5c070fff/E-ISAC_SANS_Ukraine_DUC_5%5b73%5d.pdf
Emerson Exchange | Emerson Exchange Increase Security with TPM, Secure Boot, and Trusted Boot Retrieved. 2020/09/25 | https://emersonexchange365.com/products/control-safety-systems/f/plc-pac-systems-industrial-computing-forum/8383/increase-security-with-tpm-secure-boot-and-trusted-boot
Enterprise ATT&CK | Enterprise ATT&CK Enterprise ATT&CK Service Stop Retrieved. 2019/10/29 Service Stop Retrieved. 2019/10/29 | https://attack.mitre.org/techniques/T1489/
Enterprise ATT&CK January 2018 | Enterprise ATT&CK 2018, January 11 Command-Line Interface Retrieved. 2018/05/17 | https://attack.mitre.org/wiki/Technique/T1059
Enterprise ATT&CK October 2019 | Enterprise ATT&CK 2019, October 25 Spearphishing Attachment Retrieved. 2019/10/25 | https://attack.mitre.org/techniques/T1193/
EyeofRa Detecting Hooking June 2017 | Eye of Ra. (2017, June 27). Windows Keylogger Part 2: Defense against user-land. Retrieved December 12, 2017. | https://eyeofrablog.wordpress.com/2017/06/27/windows-keylogger-part-2-defense-against-user-land/
F-Secure BlackEnergy 2014 | F-Secure Labs. (2014). BlackEnergy & Quedagh: The convergence of crimeware and APT attacks. Retrieved March 24, 2016. | https://blog-assets.f-secure.com/wp-content/uploads/2019/10/15163408/BlackEnergy_Quedagh.pdf
FBI Flash FIN7 USB | The Record. (2022, January 7). FBI: FIN7 hackers target US companies with BadUSB devices to install ransomware. Retrieved January 14, 2022. | https://therecord.media/fbi-fin7-hackers-target-us-companies-with-badusb-devices-to-install-ransomware/
FireEye APT33 Sept 2017 | O'Leary, J., et al. (2017, September 20). Insights into Iranian Cyber Espionage: APT33 Targets Aerospace and Energy Sectors and has Ties to Destructive Malware. Retrieved February 15, 2018. | https://www.fireeye.com/blog/threat-research/2017/09/apt33-insights-into-iranian-cyber-espionage.html
FireEye APT33 Webinar Sept 2017 | Davis, S. and Carr, N. (2017, September 21). APT33: New Insights into Iranian Cyber Espionage Group. Retrieved February 15, 2018. | https://www.brighttalk.com/webcast/10703/275683
FireEye APT34 Dec 2017 | Sardiwal, M, et al. (2017, December 7). New Targeted Attack in the Middle East by APT34, a Suspected Iranian Threat Group, Using CVE-2017-11882 Exploit. Retrieved December 20, 2017. | https://www.fireeye.com/blog/threat-research/2017/12/targeted-attack-in-middle-east-by-apt34.html
FireEye APT38 Oct 2018 | FireEye. (2018, October 03). APT38: Un-usual Suspects. Retrieved November 6, 2018. | https://content.fireeye.com/apt/rpt-apt38
FireEye CARBANAK June 2017 | Bennett, J., Vengerik, B. (2017, June 12). Behind the CARBANAK Backdoor. Retrieved June 11, 2018. | https://www.fireeye.com/blog/threat-research/2017/06/behind-the-carbanak-backdoor.html
FireEye FIN6 Apr 2019 | McKeague, B. et al. (2019, April 5). Pick-Six: Intercepting a FIN6 Intrusion, an Actor Recently Tied to Ryuk and LockerGoga Ransomware. Retrieved April 17, 2019. | https://www.fireeye.com/blog/threat-research/2019/04/pick-six-intercepting-a-fin6-intrusion.html
FireEye FIN6 April 2016 | FireEye Threat Intelligence. (2016, April). Follow the Money: Dissecting the Operations of the Cyber Crime Group FIN6. Retrieved June 1, 2016. | https://www2.fireeye.com/rs/848-DID-242/images/rpt-fin6.pdf
FireEye FIN7 April 2017 | Carr, N., et al. (2017, April 24). FIN7 Evolution and the Phishing LNK. Retrieved April 24, 2017. | https://www.fireeye.com/blog/threat-research/2017/04/fin7-phishing-lnk.html
FireEye FIN7 Aug 2018 | Carr, N., et al. (2018, August 01). On the Hunt for FIN7: Pursuing an Enigmatic and Evasive Global Criminal Operation. Retrieved August 23, 2018. | https://www.fireeye.com/blog/threat-research/2018/08/fin7-pursuing-an-enigmatic-and-evasive-global-criminal-operation.html
FireEye FIN7 March 2017 | Miller, S., et al. (2017, March 7). FIN7 Spear Phishing Campaign Targets Personnel Involved in SEC Filings. Retrieved March 8, 2017. | https://web.archive.org/web/20180808125108/https:/www.fireeye.com/blog/threat-research/2017/03/fin7_spear_phishing.html
FireEye FIN7 Shim Databases | Erickson, J., McWhirt, M., Palombo, D. (2017, May 3). To SDB, Or Not To SDB: FIN7 Leveraging Shim Databases for Persistence. Retrieved July 18, 2017. | https://www.fireeye.com/blog/threat-research/2017/05/fin7-shim-databases-persistence.html
FireEye KEGTAP SINGLEMALT October 2020 | Kimberly Goody, Jeremy Kennelly, Joshua Shilko, Steve Elovitz, Douglas Bienstock. (2020, October 28). Unhappy Hour Special: KEGTAP and SINGLEMALT With a Ransomware Chaser. Retrieved October 28, 2020. | https://www.fireeye.com/blog/threat-research/2020/10/kegtap-and-singlemalt-with-a-ransomware-chaser.html
FireEye PowerShell Logging | Dunwoody, M. (2016, February 11). Greater Visibility Through PowerShell Logging. Retrieved September 28, 2021. | https://www.fireeye.com/blog/threat-research/2016/02/greater_visibilityt.html
FireEye Ransomware Feb 2020 | Zafra, D., et al. (2020, February 24). Ransomware Against the Machine: How Adversaries are Learning to Disrupt Industrial Production by Targeting IT and OT. Retrieved March 2, 2021. | https://www.fireeye.com/blog/threat-research/2020/02/ransomware-against-machine-learning-to-disrupt-industrial-production.html
FireEye Ryuk and Trickbot January 2019 | Goody, K., et al (2019, January 11). A Nasty Trick: From Credential Theft Malware to Business Disruption. Retrieved May 12, 2020. | https://www.fireeye.com/blog/threat-research/2019/01/a-nasty-trick-from-credential-theft-malware-to-business-disruption.html
FireEye TEMP.Veles 2018 | FireEye Intelligence . (2018, October 23). TRITON Attribution: Russian Government-Owned Lab Most Likely Built Custom Intrusion Tools for TRITON Attackers. Retrieved April 16, 2019. | https://www.fireeye.com/blog/threat-research/2018/10/triton-attribution-russian-government-owned-lab-most-likely-built-tools.html
FireEye TEMP.Veles JSON April 2019 | Miller, S., et al. (2019, April 10). TRITON Appendix C. Retrieved April 29, 2019. | https://www.fireeye.com/content/dam/fireeye-www/blog/files/TRITON_Appendix_C.html
FireEye TRITON | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer. (2017, December 14). Attackers Deploy New ICS Attack Framework "TRITON" and Cause Operational Disruption to Critical Infrastructure. Retrieved January 6, 2021. | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
FireEye TRITON 2017 | Johnson, B, et. al. (2017, December 14). Attackers Deploy New ICS Attack Framework "TRITON" and Cause Operational Disruption to Critical Infrastructure. Retrieved January 6, 2021. | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
FireEye TRITON 2018 | Miller, S. Reese, E. (2018, June 7). A Totally Tubular Treatise on TRITON and TriStation. Retrieved January 6, 2021. | https://www.fireeye.com/blog/threat-research/2018/06/totally-tubular-treatise-on-TRITON-and-tristation.html
FireEye TRITON 2019 | Miller, S, et al. (2019, April 10). TRITON Actor TTP Profile, Custom Attack Tools, Detections, and ATT&CK Mapping. Retrieved April 16, 2019. | https://www.fireeye.com/blog/threat-research/2019/04/triton-actor-ttp-profile-custom-attack-tools-detections.html
FireEye TRITON Dec 2017 | Blake Johnson, Dan Caban, Marina Krotofil, Dan Scali, Nathan Brubaker, Christopher Glyer. (2017, December 14). Attackers Deploy New ICS Attack Framework “TRITON” and Cause Operational Disruption to Critical Infrastructure. Retrieved January 12, 2018. | https://www.fireeye.com/blog/threat-research/2017/12/attackers-deploy-new-ics-attack-framework-triton.html
FireEye WannaCry 2017 | Berry, A., Homan, J., and Eitzman, R. (2017, May 23). WannaCry Malware Profile. Retrieved March 15, 2019. | https://www.fireeye.com/blog/threat-research/2017/05/wannacry-malware-profile.html
Fortune Dragonfly 2.0 Sept 2017 | Hackett, R. (2017, September 6). Hackers Have Penetrated Energy Grid, Symantec Warns. Retrieved June 6, 2018. | http://fortune.com/2017/09/06/hack-energy-grid-symantec/
Frank Bajak and Marc Levy December 2023 | Frank Bajak and Marc Levy. (2023, December 2). Breaches by Iran-affiliated hackers spanned multiple U.S. states, federal agencies say. Retrieved March 25, 2024. | https://apnews.com/article/hackers-iran-israel-water-utilities-critical-infrastructure-cisa-554b2aa969c8220016ab2ef94bd7635b
G Data Sodinokibi June 2019 | Han, Karsten. (2019, June 4). Strange Bits: Sodinokibi Spam, CinaRAT, and Fake G DATA. Retrieved August 4, 2020. | https://www.gdatasoftware.com/blog/2019/06/31724-strange-bits-sodinokibi-spam-cinarat-and-fake-g-data
GTFO split | GTFOBins. (2020, November 13). split. Retrieved April 18, 2022. | https://gtfobins.github.io/gtfobins/split/
Gabriel Sanchez October 2017 | Gabriel Sanchez 2017, October Man-In-The-Middle Attack Against Modbus TCP Illustrated with Wireshark Retrieved. 2020/01/05 | https://www.sans.org/reading-room/whitepapers/ICS/man-in-the-middle-attack-modbus-tcp-illustrated-wireshark-38095
Gallagher, S. April 2017 | Gallagher, S. 2017, April 12 Pirate radio: Signal spoof set off Dallas emergency sirens, not network hack Retrieved. 2020/12/01 | https://arstechnica.com/information-technology/2017/04/dallas-siren-hack-used-radio-signals-to-spoof-alarm-says-city-manager/
Gardiner, J., Cova, M., Nagaraja, S February 2014 | Gardiner, J., Cova, M., Nagaraja, S 2014, February Command & Control Understanding, Denying and Detecting Retrieved. 2016/04/20 | https://arxiv.org/ftp/arxiv/papers/1408/1408.1136.pdf
German BAS Lockout Dec 2021 | Kelly Jackson Higgins. (2021, December 20). Lights Out: Cyberattacks Shut Down Building Automation Systems. Retrieved March 30, 2023. | https://www.darkreading.com/attacks-breaches/lights-out-cyberattacks-shut-down-building-automation-systems
Gigamon Berserk Bear October 2021 | Slowik, J. (2021, October). THE BAFFLING BERSERK BEAR: A DECADE’S ACTIVITY TARGETING CRITICAL INFRASTRUCTURE. Retrieved December 6, 2021. | https://vblocalhost.com/uploads/VB2021-Slowik.pdf
Github CHIPSEC | Intel. (2017, March 18). CHIPSEC Platform Security Assessment Framework. Retrieved March 20, 2017. | https://github.com/chipsec/chipsec
Group IB Ransomware May 2020 | Group IB. (2020, May). Ransomware Uncovered: Attackers’ Latest Methods. Retrieved August 5, 2020. | https://www.group-ib.com/whitepapers/ransomware-uncovered.html
Guidance - NIST SP800-82 | Keith Stouffer. (2015, May). Guide to Industrial Control Systems (ICS) Security. Retrieved March 28, 2018. | https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-82r2.pdf
HIDDEN COBRA | The U.S. Government refers to malicious cyber activity by the North Korean government as HIDDEN COBRA.(Citation: US-CERT HIDDEN COBRA June 2017)(Citation: US-CERT HOPLIGHT Apr 2019)
Hydro | Hydro Kevin Beaumont How Lockergoga took down Hydro ransomware used in targeted attacks aimed at big business Retrieved. 2019/10/16 Retrieved. 2019/10/16 | https://www.hydro.com/en/media/on-the-agenda/cyber-attack/
IBM Ransomware Trends September 2020 | Singleton, C. and Kiefer, C. (2020, September 28). Ransomware 2020: Attack Trends Affecting Organizations Worldwide. Retrieved September 20, 2021. | https://securityintelligence.com/posts/ransomware-2020-attack-trends-new-techniques-affecting-organizations-worldwide/
IBM X-Force ITG23 Oct 2021 | Villadsen, O., et al. (2021, October 13). Trickbot Rising - Gang Doubles Down on Infection Efforts to Amass Network Footholds. Retrieved June 15, 2023. | https://securityintelligence.com/posts/trickbot-gang-doubles-down-enterprise-infection/
ICS CERT September 2018 | ICS CERT 2018, September 06 Advantech/Broadwin WebAccess RPC Vulnerability (Update B) Retrieved. 2019/12/05 | https://www.us-cert.gov/ics/advisories/ICSA-11-094-02B
ICS-CERT April 2017 | ICS-CERT 2017, April 18 CS Alert (ICS-ALERT-17-102-01A) BrickerBot Permanent Denial-of-Service Attack Retrieved. 2019/10/24 | https://www.us-cert.gov/ics/alerts/ICS-ALERT-17-102-01A
ICS-CERT August 2018 | ICS-CERT 2018, August 22 Advisory (ICSA-14-178-01) Retrieved. 2019/04/01 | https://ics-cert.us-cert.gov/advisories/ICSA-14-178-01
ICS-CERT December 2014 | ICS-CERT 2014, December 10 ICS Alert (ICS-ALERT-14-281-01E) Ongoing Sophisticated Malware Campaign Compromising ICS (Update E) Retrieved. 2019/10/11 | https://www.us-cert.gov/ics/alerts/ICS-ALERT-14-281-01B
ICS-CERT December 2018 | ICS-CERT 2018, December 18 Advisory (ICSA-18-107-02) - Schneider Electric Triconex Tricon (Update B) Retrieved. 2019/03/08 | https://ics-cert.us-cert.gov/advisories/ICSA-18-107-02
ICS-CERT October 2017 | ICS-CERT 2017, October 21 Advanced Persistent Threat Activity Targeting Energy and Other Critical Infrastructure Sectors Retrieved. 2017/10/23 | https://www.us-cert.gov/ncas/alerts/TA17-293A
IEC August 2013 | IEC 2013, August Industrial communication networks - Network and system security - Part 3-3: System security requirements and security levels Retrieved. 2020/09/25 | https://webstore.iec.ch/publication/7033
IEC February 2013 | IEC 2013, February 20 IEC 61131-3:2013 Programmable controllers - Part 3: Programming languages Retrieved. 2019/10/22 | https://webstore.iec.ch/publication/4552
IEC February 2019 | IEC 2019, February Security for industrial automation and control systems - Part 4-2: Technical security requirements for IACS components Retrieved. 2020/09/25 | https://webstore.iec.ch/publication/34421
IETF RFC4949 2007 | Internet Engineering Task Force. (2007, August). Internet Security Glossary, Version 2. Retrieved September 29, 2023. | https://www.ietf.org/rfc/rfc4949.txt
ITG14 | ITG14 shares campaign overlap with [FIN7](https://attack.mitre.org/groups/G0046).(Citation: IBM Ransomware Trends September 2020)
Industroyer2 Blackhat ESET | Anton Cherepanov, Robert Lipovsky. (2022, August). Industroyer2: Sandworm's Cyberwarfare Targets Ukraine's Power Grid. Retrieved April 6, 2023. | https://www.youtube.com/watch?v=xC9iM5wVedQ
Industroyer2 ESET April 2022 | ESET. (2022, April 12). Industroyer2: Industroyer reloaded. Retrieved March 30, 2023. | https://www.welivesecurity.com/2022/04/12/industroyer2-industroyer-reloaded/
Industroyer2 Forescout July 2022 | Forescout. (2022, July 14). Industroyer2 and INCONTROLLER In-depth Technical Analysis of the Most Recent ICS-specific Malware. Retrieved March 30, 2023. | https://www.forescout.com/resources/industroyer2-and-incontroller-report/
Industroyer2 Mandiant April 2022 | Daniel Kapellmann Zafra, Raymond Leong, Chris Sistrunk, Ken Proska, Corey Hildebrandt, Keith Lunden, Nathan Brubaker. (2022, April 25). INDUSTROYER.V2: Old Malware Learns New Tricks. Retrieved March 30, 2023. | https://www.mandiant.com/resources/blog/industroyer-v2-old-malware-new-tricks
InfoSecurity Sandworm Oct 2014 | Muncaster, P.. (2014, October 14). Microsoft Zero Day Traced to Russian ‘Sandworm’ Hackers. Retrieved October 6, 2017. | https://www.infosecurity-magazine.com/news/microsoft-zero-day-traced-russian/
Institute of Electrical and Electronics Engineers January 2014 | Institute of Electrical and Electronics Engineers 2014, January 1686-2013 - IEEE Standard for Intelligent Electronic Devices Cyber Security Capabilities Retrieved. 2020/09/17 | https://standards.ieee.org/standard/1686-2013.html
Intel | Intel ESET Research Whitepapers 2018, September LOJAX First UEFI rootkit found in the wild, courtesy of the Sednit group Retrieved. 2020/09/25 Intel Hardware-based Security Technologies for Intelligent Retail Devices Retrieved. 2020/09/25 | https://www.intel.com/content/dam/www/public/us/en/documents/white-papers/security-technologies-4th-gen-core-retail-paper.pdf
Intel 471 REvil March 2020 | Intel 471 Malware Intelligence team. (2020, March 31). REvil Ransomware-as-a-Service – An analysis of a ransomware affiliate operation. Retrieved August 4, 2020. | https://intel471.com/blog/revil-ransomware-as-a-service-an-analysis-of-a-ransomware-affiliate-operation/
Intel HackingTeam UEFI Rootkit | Intel Security. (2005, July 16). HackingTeam's UEFI Rootkit Details. Retrieved March 20, 2017. | http://www.intelsecurity.com/advanced-threat-research/content/data/HT-UEFI-rootkit.html
International Electrotechnical Commission July 2020 | International Electrotechnical Commission 2020, July 17 IEC 62351 - Power systems management and associated information exchange - Data and communications security Retrieved. 2020/09/17 | https://webstore.iec.ch/publication/6912
Jacqueline O'Leary et al. September 2017 | Jacqueline O'Leary et al. 2017, September 20 Insights into Iranian Cyber Espionage: APT33 Targets Aerospace and Energy Sectors and has Ties to Destructive Malware Retrieved. 2019/12/02 | https://www.fireeye.com/blog/threat-research/2017/09/apt33-insights-into-iranian-cyber-espionage.html
Jamie Tarabay and Katrina Manson December 2023 | Jamie Tarabay and Katrina Manson. (2023, December 22). Iranian-Linked Hacks Expose Failure to Safeguard US Water System. Retrieved March 25, 2024. | https://www.bloomberg.com/news/articles/2023-12-22/iranian-linked-hacks-expose-failure-to-safeguard-us-water-system
Jay GetHooks Sept 2011 | Satiro, J. (2011, September 14). GetHooks. Retrieved December 12, 2017. | https://github.com/jay/gethooks
Jeff Jones May 2018 | Jeff Jones 2018, May 10 Dragos Releases Details on Suspected Russian Infrastructure Hacking Team ALLANITE Retrieved. 2020/01/03 | https://www.eisac.com/public-news-detail?id=115909
Joe Slowik April 2019 | Joe Slowik 2019, April 10 Implications of IT Ransomware for ICS Environments Retrieved. 2019/10/27 | https://dragos.com/blog/industry-news/implications-of-it-ransomware-for-ics-environments/
Joe Slowik August 2019 | Joe Slowik 2019, August 15 CRASHOVERRIDE: Reassessing the 2016 Ukraine Electric Power Event as a Protection-Focused Attack Retrieved. 2019/10/22 | https://dragos.com/wp-content/uploads/CRASHOVERRIDE.pdf
John Bill May 2017 | John Bill 2017, May 12 Hacked Cyber Security Railways Retrieved. 2019/10/17 | https://www.londonreconnections.com/2017/hacked-cyber-security-railways/
Jos Wetzels January 2018 | Jos Wetzels 2018, January 16 Analyzing the TRITON industrial malware Retrieved. 2019/10/22 | https://www.midnightbluelabs.com/blog/2018/1/16/analyzing-the-triton-industrial-malware
Jos Wetzels, Marina Krotofil 2019 | Jos Wetzels, Marina Krotofil 2019 A Diet of Poisoned Fruit: Designing Implants & OT Payloads for ICS Embedded Devices Retrieved. 2019/11/01 | https://troopers.de/downloads/troopers19/TROOPERS19_NGI_IoT_diet_poisoned_fruit.pdf
Josh Rinaldi April 2016 | Josh Rinaldi 2016, April Still a Thrill: OPC UA Device Discovery Retrieved. 2020/09/25 | https://www.rtautomation.com/rtas-blog/still-a-thrill-opc-ua-device-discovery/
Julian Gutmanis March 2019 | Julian Gutmanis 2019, March 11 Triton - A Report From The Trenches Retrieved. 2019/03/11 | https://www.youtube.com/watch?v=XwSJ8hloGvY
Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell December 2015 | Julian Rrushi, Hassan Farhangi, Clay Howey, Kelly Carmichael, Joey Dabell 2015, December 08 A Quantitative Evaluation of the Target Selection of Havex ICS Malware Plugin Retrieved. 2019/04/01 | https://pdfs.semanticscholar.org/18df/43ef1690b0fae15a36f770001160aefbc6c5.pdf
Junnosuke Yagi March 2017 | Junnosuke Yagi 2017, March 07 Trojan.Stonedrill Retrieved. 2019/12/05 | https://www.symantec.com/security-center/writeup/2017-030708-4403-99
Karen Scarfone; Paul Hoffman September 2009 | Karen Scarfone; Paul Hoffman 2009, September Guidelines on Firewalls and Firewall Policy Retrieved. 2020/09/25 | https://nvlpubs.nist.gov/nistpubs/Legacy/SP/nistspecialpublication800-41r1.pdf
Kaspersky Flame | Gostev, A. (2012, May 28). The Flame: Questions and Answers. Retrieved March 1, 2017. | https://securelist.com/the-flame-questions-and-answers-51/34344/
Kaspersky Lazarus Under The Hood Blog 2017 | GReAT. (2017, April 3). Lazarus Under the Hood. Retrieved April 17, 2019. | https://securelist.com/lazarus-under-the-hood/77908/
Kaspersky Lyceum October 2021 | Kayal, A. et al. (2021, October). LYCEUM REBORN: COUNTERINTELLIGENCE IN THE MIDDLE EAST. Retrieved June 14, 2022. | https://vblocalhost.com/uploads/VB2021-Kayal-etal.pdf
Kaspersky Sodin July 2019 | Mamedov, O, et al. (2019, July 3). Sodin ransomware exploits Windows vulnerability and processor architecture. Retrieved August 4, 2020. | https://securelist.com/sodin-ransomware/91473/
Keith Stouffer May 2015 | Keith Stouffer 2015, May Guide to Industrial Control Systems (ICS) Security Retrieved. 2018/03/28 | https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-82r2.pdf
Kelly Jackson Higgins | Kelly Jackson Higgins How a Manufacturing Firm Recovered from a Devastating Ransomware Attack Retrieved. 2019/11/03 | https://www.darkreading.com/attacks-breaches/how-a-manufacturing-firm-recovered-from-a-devastating-ransomware-attack/d/d-id/1334760
Kernkraftwerk Gundremmingen April 2016 | Kernkraftwerk Gundremmingen 2016, April 25 Detektion von Bro-Schadsoftware an mehreren Rechnern Retrieved. 2019/10/14 | https://www.kkw-gundremmingen.de/presse.php?id=571
Kevin Beaumont | Kevin Beaumont How Lockergoga took down Hydro ransomware used in targeted attacks aimed at big business Retrieved. 2019/10/16 | https://doublepulsar.com/how-lockergoga-took-down-hydro-ransomware-used-in-targeted-attacks-aimed-at-big-business-c666551f5880
Kevin Savage and Branko Spasojevic | Kevin Savage and Branko Spasojevic W32.Flamer Retrieved. 2019/11/03 | https://web.archive.org/web/20190930124504/https://www.symantec.com/security-center/writeup/2012-052811-0308-99
KillDisk Ransomware | Catalin Cimpanu. (2016, December 29). KillDisk Disk-Wiping Malware Adds Ransomware Component. Retrieved January 12, 2021. | https://www.bleepingcomputer.com/news/security/killdisk-disk-wiping-malware-adds-ransomware-component/
Kyle Wilhoit | Kyle Wilhoit Daavid Hentunen, Antti Tikkanen 2014, June 23 Havex Hunts For ICS/SCADA Systems Retrieved. 2019/04/01 ICS Malware: Havex and Black Energy Retrieved. 2019/10/22 | https://www.youtube.com/watch?v=eywmb7UDODY&feature=youtu.be&t=939
LOLBAS Project | Oddvar Moe et al. (2022, February). Living Off The Land Binaries, Scripts and Libraries. Retrieved March 7, 2022. | https://github.com/LOLBAS-Project/LOLBAS#criteria
Langer Stuxnet | Ralph Langner. (2013, November). To Kill a Centrifuge: A Technical Analysis of What Stuxnet's Creators Tried to Achieve. Retrieved December 7, 2020. | https://www.langner.com/wp-content/uploads/2017/03/to-kill-a-centrifuge.pdf
Langner November 2018 | Langner 2018, November Why Ethernet/IP changes the OT asset discovery game Retrieved. 2020/09/25 | https://www.langner.com/2018/11/why-ethernet-ip-changes-the-ot-asset-discovery-game/
Lee Mathews April 2016 | Lee Mathews 2016, April 27 German nuclear plant found riddled with Conficker, other viruses Retrieved. 2019/10/14 | https://www.geek.com/apps/german-nuclear-plant-found-riddled-with-conficker-other-viruses-1653415/
Leonard TAG 2023 | Billy Leonard. (2023, April 19). Ukraine remains Russia’s biggest cyber focus in 2023. Retrieved March 1, 2024. | https://blog.google/threat-analysis-group/ukraine-remains-russias-biggest-cyber-focus-in-2023/
Linux Services Run Levels | The Linux Foundation. (2006, January 11). An introduction to services, runlevels, and rc.d scripts. Retrieved September 28, 2021. | https://www.linux.com/news/introduction-services-runlevels-and-rcd-scripts/
Lion Corporation June 2020 | Lion Corporation 2020, June 26 Lion Cyber incident update: 26 June 2020 Retrieved. 2021/10/08 | https://lionco.com/2020/06/26/lion-update-re-cyber-issue/
Lisa Zahner December 2023 | Lisa Zahner. (2023, December 15). Hackers in Iran attack computer at Vero Utilities. Retrieved March 25, 2024. | https://veronews.com/2023/12/15/hackers-in-iran-attack-computer-at-vero-utilities/
LogRhythm WannaCry | Noerenberg, E., Costis, A., and Quist, N. (2017, May 16). A Technical Analysis of WannaCry Ransomware. Retrieved March 25, 2019. | https://logrhythm.com/blog/a-technical-analysis-of-wannacry-ransomware/
M. Rentschler and H. Heine | M. Rentschler and H. Heine The Parallel Redundancy Protocol for industrial IP networks Retrieved. 2020/09/25 | https://ieeexplore.ieee.org/document/6505877
MDudek-ICS | MDudek-ICS TRISIS-TRITON-HATMAN Retrieved. 2019/11/03 | https://github.com/MDudek-ICS/TRISIS-TRITON-HATMAN/tree/master/decompiled_code/library
MITRE | MITRE System Network Connections Discovery Retrieved. 2018/05/31 | https://attack.mitre.org/wiki/Technique/T1049
MITRE Copernicus | Butterworth, J. (2013, July 30). Copernicus: Question Your Assumptions about BIOS Security. Retrieved December 11, 2015. | http://www.mitre.org/capabilities/cybersecurity/overview/cybersecurity-blog/copernicus-question-your-assumptions-about
MITRE June 2020 | MITRE 2020, June CWE CATEGORY: 7PK - API Abuse Retrieved. 2020/09/25 | https://cwe.mitre.org/data/definitions/227.html
MITRE March 2018 | MITRE 2018, March 22 CVE-2015-5374 Retrieved. 2019/03/14 | https://nvd.nist.gov/vuln/detail/CVE-2015-5374
Machine Information Systems 2007 | Machine Information Systems 2007 How PLCs Work Retrieved. 2021/01/28 | http://www.machine-information-systems.com/How_PLCs_Work.html
Mandiant FIN12 Oct 2021 | Shilko, J., et al. (2021, October 7). FIN12: The Prolific Ransomware Intrusion Threat Actor That Has Aggressively Pursued Healthcare Targets. Retrieved June 15, 2023. | https://www.mandiant.com/sites/default/files/2021-10/fin12-group-profile.pdf
Mandiant FIN7 Apr 2022 | Abdo, B., et al. (2022, April 4). FIN7 Power Hour: Adversary Archaeology and the Evolution of FIN7. Retrieved April 5, 2022. | https://www.mandiant.com/resources/evolution-of-fin7
Mandiant Ukraine Cyber Threats January 2022 | Hultquist, J. (2022, January 20). Anticipating Cyber Threats as the Ukraine Crisis Escalates. Retrieved January 24, 2022. | https://www.mandiant.com/resources/ukraine-crisis-cyber-threats
Mandiant-Sandworm-Ukraine-2022 | Ken Proska, John Wolfram, Jared Wilson, Dan Black, Keith Lunden, Daniel Kapellmann Zafra, Nathan Brubaker, Tyler Mclellan, Chris Sistrunk. (2023, November 9). Sandworm Disrupts Power in Ukraine Using a Novel Attack Against Operational Technology. Retrieved March 28, 2024. | https://www.mandiant.com/resources/blog/sandworm-disrupts-power-ukraine-operational-technology
Marc-Etienne M.Lveill October 2017 | Marc-Etienne M.Lveill 2017, October 24 Bad Rabbit: NotPetya is back with improved ransomware Retrieved. 2019/10/27 | https://www.welivesecurity.com/2017/10/24/bad-rabbit-not-petya-back/
Mark Loveless April 2017 | Mark Loveless 2017, April 11 THE DALLAS COUNTY SIREN HACK Retrieved. 2020/11/06 | https://duo.com/decipher/the-dallas-county-siren-hack
Mark Thompson March 2016 | Mark Thompson 2016, March 24 Iranian Cyber Attack on New York Dam Shows Future of War Retrieved. 2019/11/07 | https://time.com/4270728/iran-cyber-attack-dam-fbi/
Marshall Abrams July 2008 | Marshall Abrams 2008, July 23 Malicious Control System Cyber Security Attack Case Study Maroochy Water Services, Australia Retrieved. 2018/03/27 | https://www.mitre.org/sites/default/files/pdf/08_1145.pdf
Max Heinemeyer February 2020 | Max Heinemeyer 2020, February 21 Post-mortem of a targeted Sodinokibi ransomware attack Retrieved. 2021/04/12 | https://www.darktrace.com/en/blog/post-mortem-of-a-targeted-sodinokibi-ransomware-attack/
McAfee CHIPSEC Blog | Beek, C., Samani, R. (2017, March 8). CHIPSEC Support Against Vault 7 Disclosure Scanning. Retrieved March 13, 2017. | https://securingtomorrow.mcafee.com/business/chipsec-support-vault-7-disclosure-scanning/
McAfee Labs October 2019 | McAfee Labs 2019, October 02 McAfee ATR Analyzes Sodinokibi aka REvil Ransomware-as-a-Service What The Code Tells Us Retrieved. 2021/04/12 | https://www.mcafee.com/blogs/other-blogs/mcafee-labs/mcafee-atr-analyzes-sodinokibi-aka-revil-ransomware-as-a-service-what-the-code-tells-us
McAfee REvil October 2019 | Saavedra-Morales, J, et al. (2019, October 20). McAfee ATR Analyzes Sodinokibi aka REvil Ransomware-as-a-Service – Crescendo. Retrieved August 5, 2020. | https://www.mcafee.com/blogs/other-blogs/mcafee-labs/mcafee-atr-analyzes-sodinokibi-aka-revil-ransomware-as-a-service-crescendo/
McAfee Sodinokibi October 2019 | McAfee. (2019, October 2). McAfee ATR Analyzes Sodinokibi aka REvil Ransomware-as-a-Service – What The Code Tells Us. Retrieved August 4, 2020. | https://www.mcafee.com/blogs/other-blogs/mcafee-labs/mcafee-atr-analyzes-sodinokibi-aka-revil-ransomware-as-a-service-what-the-code-tells-us/
McCarthy, J et al. July 2018 | McCarthy, J et al. 2018, July NIST SP 1800-2 Identity and Access Management for Electric Utilities Retrieved. 2020/09/17 | https://doi.org/10.6028/NIST.SP.1800-2
Michael J. Assante and Robert M. Lee | Michael J. Assante and Robert M. Lee Corero Industrial Control System (ICS) Security Retrieved. 2019/11/04 The Industrial Control System Cyber Kill Chain Retrieved. 2019/11/04 | https://www.sans.org/reading-room/whitepapers/ICS/industrial-control-system-cyber-kill-chain-36297
Microsoft AMSI | Microsoft. (2019, April 19). Antimalware Scan Interface (AMSI). Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/windows/win32/amsi/antimalware-scan-interface-portal
Microsoft Anti Spoofing | Microsoft. (2020, October 13). Anti-spoofing protection in EOP. Retrieved October 19, 2020. | https://docs.microsoft.com/en-us/microsoft-365/security/office-365-security/anti-spoofing-protection?view=o365-worldwide
Microsoft Audit Logon Events | Microsoft. (2021, September 6). Audit logon events. Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/windows/security/threat-protection/auditing/basic-audit-logon-events
Microsoft August 2018 | Microsoft 2018, August Implementing Least-Privilege Administrative Models Retrieved. 2020/09/25 | https://docs.microsoft.com/en-us/windows-server/identity/ad-ds/plan/security-best-practices/implementing-least-privilege-administrative-models
Microsoft February 2019 | Microsoft 2019, February Active Directory administrative tier model Retrieved. 2020/09/25 | https://docs.microsoft.com/en-us/windows-server/identity/securing-privileged-access/securing-privileged-access-reference-material#a-nameesaebmaesae-administrative-forest-design-approach
Microsoft File Mgmt | Microsoft. (2018, May 31). File Management (Local File Systems). Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/windows/win32/fileio/file-management
Microsoft Holmium June 2020 | Microsoft Threat Protection Intelligence Team. (2020, June 18). Inside Microsoft Threat Protection: Mapping attack chains from cloud to endpoint. Retrieved June 22, 2020. | https://www.microsoft.com/security/blog/2020/06/18/inside-microsoft-threat-protection-mapping-attack-chains-from-cloud-to-endpoint/
Microsoft Hook Overview | Microsoft. (n.d.). Hooks Overview. Retrieved December 12, 2017. | https://msdn.microsoft.com/library/windows/desktop/ms644959.aspx
Microsoft LoadLibrary | Microsoft. (2018, December 5). LoadLibraryA function (libloaderapi.h). Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/windows/win32/api/libloaderapi/nf-libloaderapi-loadlibrarya
Microsoft May 2017 | Microsoft 2017, May Attractive Accounts for Credential Theft Retrieved. 2020/09/25 | https://docs.microsoft.com/en-us/windows-server/identity/ad-ds/plan/security-best-practices/attractive-accounts-for-credential-theft
Microsoft Module Class | Microsoft. (n.d.). Module Class. Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/dotnet/api/system.reflection.module
Microsoft NFS Overview | Microsoft. (2018, July 9). Network File System overview. Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/windows-server/storage/nfs/nfs-overview
Microsoft PowerShell Logging | Microsoft. (2020, March 30). about_Logging_Windows. Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/powershell/module/microsoft.powershell.core/about/about_logging_windows?view=powershell-7
Microsoft Prestige ransomware October 2022 | MSTIC. (2022, October 14). New “Prestige” ransomware impacts organizations in Ukraine and Poland. Retrieved January 19, 2023. | https://www.microsoft.com/en-us/security/blog/2022/10/14/new-prestige-ransomware-impacts-organizations-in-ukraine-and-poland/
Microsoft Processes and Threads | Microsoft. (2018, May 31). Processes and Threads. Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/windows/win32/procthread/processes-and-threads
Microsoft Ransomware as a Service | Microsoft. (2022, May 9). Ransomware as a service: Understanding the cybercrime gig economy and how to protect yourself. Retrieved March 10, 2023. | https://www.microsoft.com/en-us/security/blog/2022/05/09/ransomware-as-a-service-understanding-the-cybercrime-gig-economy-and-how-to-protect-yourself/
Microsoft Registry | Microsoft. (2018, May 31). Registry. Retrieved September 29, 2021. | https://docs.microsoft.com/en-us/windows/win32/sysinfo/registry
Microsoft Security Response Center August 2017 | Microsoft Security Response Center 2017, August Moving Beyond EMET II Windows Defender Exploit Guard Retrieved. 2020/09/25 | https://msrc-blog.microsoft.com/2017/08/09/moving-beyond-emet-ii-windows-defender-exploit-guard/
Microsoft Services | Microsoft. (2017, March 30). Introduction to Windows Service Applications. Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/dotnet/framework/windows-services/introduction-to-windows-service-applications
Microsoft SharePoint Logging | Microsoft. (2017, July 19). Configure audit settings for a site collection. Retrieved April 4, 2018. | https://support.office.com/en-us/article/configure-audit-settings-for-a-site-collection-a9920c97-38c0-44f2-8bcb-4cf1e2ae22d2
Microsoft Tasks | Microsoft. (2018, May 31). Tasks. Retrieved September 28, 2021. | https://docs.microsoft.com/en-us/windows/win32/taskschd/tasks
Microsoft Threat Actor Naming July 2023 | Microsoft . (2023, July 12). How Microsoft names threat actors. Retrieved November 17, 2023. | https://learn.microsoft.com/en-us/microsoft-365/security/intelligence/microsoft-threat-actor-naming?view=o365-worldwide
Microsoft ZINC disruption Dec 2017 | Smith, B. (2017, December 19). Microsoft and Facebook disrupt ZINC malware attack to protect customers and the internet from ongoing cyberthreats. Retrieved December 20, 2017. | https://blogs.microsoft.com/on-the-issues/2017/12/19/microsoft-facebook-disrupt-zinc-malware-attack-protect-customers-internet-ongoing-cyberthreats/
Morphisec FIN7 June 2017 | Gorelik, M.. (2017, June 9). FIN7 Takes Another Bite at the Restaurant Industry. Retrieved July 13, 2017. | http://blog.morphisec.com/fin7-attacks-restaurant-industry
N.A. October 2017 | N.A. 2017, October What are the different operating modes in PLC? Retrieved. 2021/01/28 | https://forumautomation.com/t/what-are-the-different-operating-modes-in-plc/2489
N/A | N/A Trusted Platform Module (TPM) Summary Retrieved. 2020/09/25 | https://www.trustedcomputinggroup.org/wp-content/uploads/Trusted-Platform-Module-Summary_04292008.pdf
NCCIC August 2018 | NCCIC 2018, August 2 Recommended Practice: Updating Antivirus in an Industrial Control System Retrieved. 2020/09/17 | https://us-cert.cisa.gov/sites/default/files/recommended_practices/Recommended%20Practice%20Updating%20Antivirus%20in%20an%20Industrial%20Control%20System_S508C.pdf
NCCIC January 2014 | NCCIC 2014, January 1 Internet Accessible Control Systems At Risk Retrieved. 2019/11/07 | https://www.us-cert.gov/sites/default/files/Monitors/ICS-CERT_Monitor_Jan-April2014.pdf
NCSC Sandworm Feb 2020 | NCSC. (2020, February 20). NCSC supports US advisory regarding GRU intrusion set Sandworm. Retrieved June 10, 2020. | https://www.ncsc.gov.uk/news/ncsc-supports-sandworm-advisory
Nanjundaiah, Vaidyanath | Nanjundaiah, Vaidyanath Dr. Kelvin T. Erickson 2010, December Programmable logic controller hardware Retrieved. 2018/03/29 PLC Ladder Logic Basics Retrieved. 2021/10/11 | https://www.ezautomation.net/industry-articles/plc-ladder-logic-basics.htm
National Institute of Standards and Technology April 2013 | National Institute of Standards and Technology 2013, April Security and Privacy Controls for Federal Information Systems and Organizations Retrieved. 2020/09/17 | https://nvlpubs.nist.gov/nistpubs/SpecialPublications/NIST.SP.800-53r4.pdf
National Security Agency February 2016 | National Security Agency 2016, February Position Zero: Integrity Checking Windows-Based ICS/SCADA Systems Retrieved. 2020/09/25 | https://apps.nsa.gov/iaarchive/library/ia-guidance/security-configuration/industrial-control-systems/position-zero-integrity-checking-windows-based-ics-scada-systems.cfm
Netstat | Wikipedia. (n.d.). Netstat. Retrieved May 23, 2022. | https://en.wikipedia.org/wiki/Netstat
Nicolas Falliere, Liam O Murchu, Eric Chien February 2011 | Nicolas Falliere, Liam O Murchu, Eric Chien 2011, February W32.Stuxnet Dossier (Version 1.4) Retrieved. 2017/09/22 | https://www.wired.com/images_blogs/threatlevel/2011/02/Symantec-Stuxnet-Update-Feb-2011.pdf
North America Transmission Forum December 2019 | North America Transmission Forum 2019, December NATF Transient Cyber Asset Guidance Retrieved. 2020/09/25 | https://www.natf.net/docs/natf/documents/resources/security/natf-transient-cyber-asset-guidance.pdf
North American Electric Reliability Corporation June 2021 | North American Electric Reliability Corporation 2021, June 28 Glossary of Terms Used in NERC Reliability Standards Retrieved. 2021/10/11 | https://www.nerc.com/pa/Stand/Glossary%20of%20Terms/Glossary_of_Terms.pdf
Novetta Blockbuster | Novetta Threat Research Group. (2016, February 24). Operation Blockbuster: Unraveling the Long Thread of the Sony Attack. Retrieved February 25, 2016. | https://web.archive.org/web/20160226161828/https://www.operationblockbuster.com/wp-content/uploads/2016/02/Operation-Blockbuster-Report.pdf
Novetta Threat Research Group February 2016 | Novetta Threat Research Group 2016, February 24 Operation Blockbuster: Unraveling the Long Thread of the Sony Attack Retrieved. 2016/02/25 | https://www.operationblockbuster.com/wp-content/uploads/2016/02/Operation-Blockbuster-Report.pdf
Nzyme Alerts Intro | Koopmann, Lennart. (n.d.). Nzyme Alerts Introduction. Retrieved September 26, 2022. | https://www.nzyme.org/docs/alerts/intro
OWASP | OWASP Top 10 Web Application Security Risks Retrieved. 2020/09/25 | https://owasp.org/www-project-top-ten/
Omron | Omron Machine Information Systems 2007 How PLCs Work Retrieved. 2021/01/28 PLC Different Operating Modes Retrieved. 2021/01/28 | https://www.omron-ap.com/service_support/FAQ/FAQ00002/index.asp#:~:text=In%20PROGRAM%20mode%2C%20the%20CPU,can%20be%20created%20or%20modified.
Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov October 2017 | Orkhan Mamedov, Fedor Sinitsyn, Anton Ivanov 2017, October 27 Bad Rabbit Ransomware Retrieved. 2019/10/27 | https://securelist.com/bad-rabbit-ransomware/82851/
PLCTop20 Mar 2023 | PLC Security, Top 20 Community. (2021, June 15). Secure PLC Coding Practices: Top 20 version 1.0. Retrieved March 22, 2023. | https://plc-security.com/content/Top_20_Secure_PLC_Coding_Practices_V1.0.pdf
PLCdev | PLCdev Nicolas Falliere, Liam O Murchu, Eric Chien 2011, February W32.Stuxnet Dossier (Version 1.4) Retrieved. 2017/09/22 Siemens SIMATIC Step 7 Programmer's Handbook Retrieved. 2019/11/21 | http://www.plcdev.com/book/export/html/373
PLCgurus 2021 | PLCgurus 2021 PLC Basics Modes Of Operation Retrieved. 2021/01/28 | https://www.plcgurus.net/plc-basics/
Paganini, Pierluigi June 2020 | Paganini, Pierluigi 2020, June 14 Ransomware attack disrupts operations at Australian beverage company Lion Retrieved. 2021/10/08 | https://securityaffairs.co/wordpress/104749/cyber-crime/ransomware-attack-hit-lion.html
Palo Alto OilRig April 2017 | Falcone, R.. (2017, April 27). OilRig Actors Provide a Glimpse into Development and Testing Efforts. Retrieved May 3, 2017. | http://researchcenter.paloaltonetworks.com/2017/04/unit42-oilrig-actors-provide-glimpse-development-testing-efforts/
Palo Alto OilRig May 2016 | Falcone, R. and Lee, B.. (2016, May 26). The OilRig Campaign: Attacks on Saudi Arabian Organizations Deliver Helminth Backdoor. Retrieved May 3, 2017. | http://researchcenter.paloaltonetworks.com/2016/05/the-oilrig-campaign-attacks-on-saudi-arabian-organizations-deliver-helminth-backdoor/
Palo Alto OilRig Oct 2016 | Grunzweig, J. and Falcone, R.. (2016, October 4). OilRig Malware Campaign Updates Toolset and Expands Targets. Retrieved May 3, 2017. | http://researchcenter.paloaltonetworks.com/2016/10/unit42-oilrig-malware-campaign-updates-toolset-and-expands-targets/
Palo Alto Unit 42 EKANS | Hinchliffe, A. Santos, D. (2020, June 26). Threat Assessment: EKANS Ransomware. Retrieved February 9, 2021. | https://unit42.paloaltonetworks.com/threat-assessment-ekans-ransomware/
Peter Dockrill April 2016 | Peter Dockrill 2016, April 28 Multiple Computer Viruses Have Been Discovered in This German Nuclear Plant Retrieved. 2019/10/14 | https://www.sciencealert.com/multiple-computer-viruses-have-been-discovered-in-this-german-nuclear-plant
Picus Sodinokibi January 2020 | Ozarslan, S. (2020, January 15). A Brief History of Sodinokibi. Retrieved August 5, 2020. | https://www.picussecurity.com/blog/a-brief-history-and-further-technical-analysis-of-sodinokibi-ransomware
PreKageo Winhook Jul 2011 | Prekas, G. (2011, July 11). Winhook. Retrieved December 12, 2017. | https://github.com/prekageo/winhook
Pylos Xenotime 2019 | Slowik, J.. (2019, April 12). A XENOTIME to Remember: Veles in the Wild. Retrieved April 16, 2019. | https://pylos.co/2019/04/12/a-xenotime-to-remember-veles-in-the-wild/
Red Canary Hospital Thwarted Ryuk October 2020 | Brian Donohue, Katie Nickels, Paul Michaud, Adina Bodkins, Taylor Chapman, Tony Lambert, Jeff Felling, Kyle Rainey, Mike Haag, Matt Graeber, Aaron Didier.. (2020, October 29). A Bazar start: How one hospital thwarted a Ryuk ransomware outbreak. Retrieved October 30, 2020. | https://redcanary.com/blog/how-one-hospital-thwarted-a-ryuk-ransomware-outbreak/
Robert A. Martin January 2021 | Robert A. Martin 2021, January TRUSTING OUR SUPPLY CHAINS: A COMPREHENSIVE DATA-DRIVEN APPROACH Retrieved. 2021/04/12 | https://www.mitre.org/sites/default/files/publications/pr-20-01465-37-trusting-our-supply-chains-a-comprehensive-data-driven-approach.pdf
Robert Falcone, Bryan Lee May 2016 | Robert Falcone, Bryan Lee 2016, May 26 The OilRig Campaign: Attacks on Saudi Arabian Organizations Deliver Helminth Backdoor Retrieved. 2019/11/19 | https://unit42.paloaltonetworks.com/the-oilrig-campaign-attacks-on-saudi-arabian-organizations-deliver-helminth-backdoor/
SANS Conficker | Burton, K. (n.d.). The Conficker Worm. Retrieved February 18, 2021. | https://web.archive.org/web/20200125132645/https://www.sans.org/security-resources/malwarefaq/conficker-worm
SIGTTO ESD 2021 | Society of International Gas Tanker & Terminal Operators Ltd. (2021). ESD Systems: Recommendations for Emergency Shutdown and Related Safety Systems (Second Edition). Retrieved September 28, 2023. | https://sigtto.org/media/3457/sigtto-2021-esd-systems.pdf
Schneider December 2018 | Schneider 2018, December 14 Security Notification EcoStruxure Triconex Tricon V3 Retrieved. 2019/03/08 | https://download.schneider-electric.com/files?p_enDocType=Technical+leaflet&p_File_Name=SEVD-2017-347-01+Triconex+V3.pdf&p_Doc_Ref=SEVD-2017-347-01
Schneider Electric January 2018 | Schneider Electric 2018, January 23 TRITON - Schneider Electric Analysis and Disclosure Retrieved. 2019/03/14 | https://www.youtube.com/watch?v=f09E75bWvkk&index=3&list=PL8OWO1qWXF4qYG19p7An4Vw3N2YZ86aRS&t=0s
Schneider-Incontroller | Schneider Electric. (2022, April 14). Schneider Electric Security Bulletin: “APT Cyber Tools Targeting ICS/SCADA Devices” . Retrieved September 28, 2022. | https://download.schneider-electric.com/files?p_Doc_Ref=SESB-2022-01
Schweitzer Engineering Laboratories August 2015 | Schweitzer Engineering Laboratories 2015, August Understanding When to Use LDAP or RADIUS for Centralized Authentication Retrieved. 2020/09/25 | https://cdn.selinc.com/assets/Literature/Publications/Application%20Notes/AN2015-08_20150817.pdf?
Sean Gallagher April 2016 | Sean Gallagher 2016, April 27 German nuclear plants fuel rod system swarming with old malware Retrieved. 2019/10/14 | https://arstechnica.com/information-technology/2016/04/german-nuclear-plants-fuel-rod-system-swarming-with-old-malware/
Secure List Bad Rabbit | Mamedov, O. Sinitsyn, F. Ivanov, A.. (2017, October 24). Bad Rabbit ransomware. Retrieved January 28, 2021. | https://securelist.com/bad-rabbit-ransomware/82851/
SecureWorks August 2019 | SecureWorks 2019, August 27 LYCEUM Takes Center Stage in Middle East Campaign Retrieved. 2019/11/19 | https://www.secureworks.com/blog/lyceum-takes-center-stage-in-middle-east-campaign
SecureWorks NICKEL GLADSTONE profile Sept 2021 | SecureWorks. (2021, September 29). NICKEL GLADSTONE Threat Profile. Retrieved September 29, 2021. | https://www.secureworks.com/research/threat-profiles/nickel-gladstone
SecureWorks September 2019 | SecureWorks 2019, September 24 REvil/Sodinokibi Ransomware Retrieved. 2021/04/12 | https://www.secureworks.com/research/revil-sodinokibi-ransomware
SecureWorks WannaCry Analysis | Counter Threat Unit Research Team. (2017, May 18). WCry Ransomware Analysis. Retrieved March 26, 2019. | https://www.secureworks.com/research/wcry-ransomware-analysis
Secureworks COBALT GYPSY Threat Profile | Secureworks. (n.d.). COBALT GYPSY Threat Profile. Retrieved April 14, 2021. | https://www.secureworks.com/research/threat-profiles/cobalt-gypsy
Secureworks GOLD NIAGARA Threat Profile | CTU. (n.d.). GOLD NIAGARA. Retrieved September 21, 2021. | https://www.secureworks.com/research/threat-profiles/gold-niagara
Secureworks GOLD SOUTHFIELD | Secureworks. (n.d.). GOLD SOUTHFIELD. Retrieved October 6, 2020. | https://www.secureworks.com/research/threat-profiles/gold-southfield
Secureworks GandCrab and REvil September 2019 | Secureworks . (2019, September 24). REvil: The GandCrab Connection. Retrieved August 4, 2020. | https://www.secureworks.com/blog/revil-the-gandcrab-connection
Secureworks Gold Blackburn Mar 2022 | Secureworks Counter Threat Unit. (2022, March 1). Gold Blackburn Threat Profile. Retrieved June 15, 2023. | https://www.secureworks.com/research/threat-profiles/gold-blackburn
Secureworks IRON LIBERTY July 2019 | Secureworks. (2019, July 24). Resurgent Iron Liberty Targeting Energy Sector. Retrieved August 12, 2020. | https://www.secureworks.com/research/resurgent-iron-liberty-targeting-energy-sector
Secureworks IRON VIKING | Secureworks. (2020, May 1). IRON VIKING Threat Profile. Retrieved June 10, 2020. | https://www.secureworks.com/research/threat-profiles/iron-viking
Secureworks IRON VIKING | Secureworks. (2020, May 1). IRON VIKING Threat Profile. Retrieved June 10, 2020. | https://www.secureworks.com/research/threat-profiles/iron-viking
Secureworks Karagany July 2019 | Secureworks. (2019, July 24). Updated Karagany Malware Targets Energy Sector. Retrieved August 12, 2020. | https://www.secureworks.com/research/updated-karagany-malware-targets-energy-sector
Secureworks MCMD July 2019 | Secureworks. (2019, July 24). MCMD Malware Analysis. Retrieved August 13, 2020. | https://www.secureworks.com/research/mcmd-malware-analysis
Secureworks NICKEL ACADEMY Dec 2017 | Secureworks. (2017, December 15). Media Alert - Secureworks Discovers North Korean Cyber Threat Group, Lazarus, Spearphishing Financial Executives of Cryptocurrency Companies. Retrieved December 27, 2017. | https://www.secureworks.com/about/press/media-alert-secureworks-discovers-north-korean-cyber-threat-group-lazarus-spearphishing
Secureworks REvil September 2019 | Counter Threat Unit Research Team. (2019, September 24). REvil/Sodinokibi Ransomware. Retrieved August 4, 2020. | https://www.secureworks.com/research/revil-sodinokibi-ransomware
Security Intelligence ITG08 April 2020 | Villadsen, O. (2020, April 7). ITG08 (aka FIN6) Partners With TrickBot Gang, Uses Anchor Framework. Retrieved October 8, 2020. | https://securityintelligence.com/posts/itg08-aka-fin6-partners-with-trickbot-gang-uses-anchor-framework/
Security Intelligence More Eggs Aug 2019 | Villadsen, O.. (2019, August 29). More_eggs, Anyone? Threat Actor ITG08 Strikes Again. Retrieved September 16, 2019. | https://securityintelligence.com/posts/more_eggs-anyone-threat-actor-itg08-strikes-again/
Selena Larson, Camille Singleton December 2020 | Selena Larson, Camille Singleton 2020, December RANSOMWARE IN ICS ENVIRONMENTS Retrieved. 2021/04/12 | https://f.hubspotusercontent10.net/hubfs/5943619/Whitepaper-Downloads/Ransomware_in_ICS_Environments_Whitepaper_10_12_20.pdf?utm_referrer=https%3A%2F%2Fwww.dragos.com%2Fresource%2Fransomware-in-ics-environments%2F
Sharepoint Sharing Events | Microsoft. (n.d.). Sharepoint Sharing Events. Retrieved October 8, 2021. | https://docs.microsoft.com/en-us/microsoft-365/compliance/use-sharing-auditing?view=o365-worldwide#sharepoint-sharing-events
Shelley Smith February 2008 | Shelley Smith 2008, February 12 Teen Hacker in Poland Plays Trains and Derails City Tram System Retrieved. 2019/10/17 | https://inhomelandsecurity.com/teen_hacker_in_poland_plays_tr/
Soldiers of Soloman | CyberAv3ngers reportedly has connections to the IRGC-linked group Soldiers of Solomon.(Citation: CISA AA23-335A IRGC-Affiliated December 2023)
Sophos New Ryuk Attack October 2020 | Sean Gallagher, Peter Mackenzie, Elida Leite, Syed Shahram, Bill Kearney, Anand Aijan, Sivagnanam Gn, Suraj Mundalik. (2020, October 14). They’re back: inside a new Ryuk ransomware attack. Retrieved October 14, 2020. | https://news.sophos.com/en-us/2020/10/14/inside-a-new-ryuk-ransomware-attack/
Spenneberg, Ralf 2016 | Spenneberg, Ralf 2016 PLC-Blaster Retrieved. 2019/06/06 | https://www.blackhat.com/docs/asia-16/materials/asia-16-Spenneberg-PLC-Blaster-A-Worm-Living-Solely-In-The-PLC.pdf
Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke March 2016 | Spenneberg, Ralf, Maik Brggemann, and Hendrik Schwartke 2016, March 31 Plc-blaster: A worm living solely in the plc. Retrieved. 2017/09/19 | https://www.blackhat.com/docs/asia-16/materials/asia-16-Spenneberg-PLC-Blaster-A-Worm-Living-Solely-In-The-PLC-wp.pdf
Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rsler, and Rainer Vosseler | Stephen Hilt, Federico Maggi, Charles Perine, Lord Remorin, Martin Rsler, and Rainer Vosseler Mark Thompson 2016, March 24 Iranian Cyber Attack on New York Dam Shows Future of War Retrieved. 2019/11/07 Caught in the Act: Running a Realistic Factory Honeypot to Capture Real Threats Retrieved. 2021/04/12 | https://documents.trendmicro.com/assets/white_papers/wp-caught-in-the-act-running-a-realistic-factory-honeypot-to-capture-real-threats.pdf
Symantec | Symantec W32.Duqu The precursor to the next Stuxnet Retrieved. 2019/11/03 | https://docs.broadcom.com/doc/w32-duqu-11-en
Symantec Beetlejuice | Symantec Security Response. (2012, May 31). Flamer: A Recipe for Bluetoothache. Retrieved February 25, 2017. | https://www.symantec.com/connect/blogs/flamer-recipe-bluetoothache
Symantec Dragonfly | Symantec Security Response. (2014, June 30). Dragonfly: Cyberespionage Attacks Against Energy Suppliers. Retrieved April 8, 2016. | https://community.broadcom.com/symantecenterprise/communities/community-home/librarydocuments/viewdocument?DocumentKey=7382dce7-0260-4782-84cc-890971ed3f17&CommunityKey=1ecf5f55-9545-44d6-b0f4-4e4a7f5f5e68&tab=librarydocuments
Symantec Dragonfly 2.0 October 2017 | Symantec. (2017, October 7). Dragonfly: Western energy sector targeted by sophisticated attack group. Retrieved April 19, 2022. | https://symantec-enterprise-blogs.security.com/blogs/threat-intelligence/dragonfly-energy-sector-cyber-attacks
Symantec Dragonfly Sept 2017 | Symantec Security Response. (2014, July 7). Dragonfly: Western energy sector targeted by sophisticated attack group. Retrieved September 9, 2017. | https://docs.broadcom.com/doc/dragonfly_threat_against_western_energy_suppliers
Symantec Elfin Mar 2019 | Security Response attack Investigation Team. (2019, March 27). Elfin: Relentless Espionage Group Targets Multiple Organizations in Saudi Arabia and U.S.. Retrieved April 10, 2019. | https://www.symantec.com/blogs/threat-intelligence/elfin-apt33-espionage
Symantec June 2015 | Symantec 2015, June 30 Simple steps to protect yourself from the Conficker Worm Retrieved. 2019/12/05 | https://support.symantec.com/us/en/article.tech93179.html
Symantec March 2019 | Symantec 2019, March 27 Elfin: Relentless Espionage Group Targets Multiple Organizations in Saudi Arabia and U.S. Retrieved. 2019/12/02 | https://www.symantec.com/blogs/threat-intelligence/elfin-apt33-espionage
Symantec Security Response July 2014 | Symantec Security Response 2014, July 7 Dragonfly: Cyberespionage Attacks Against Energy Suppliers Retrieved. 2016/04/08 | https://docs.broadcom.com/doc/dragonfly_threat_against_western_energy_suppliers#:~:text=The%20attackers%2C%20known%20to%20Symantec,supply%20in%20the%20affected%20countries.
Symantec W32.Duqu | Symantec Security Response. (2011, November). W32.Duqu: The precursor to the next Stuxnet. Retrieved September 17, 2015. | https://www.symantec.com/content/en/us/enterprise/media/security_response/whitepapers/w32_duqu_the_precursor_to_the_next_stuxnet.pdf
Sysmon EID 9 | Russinovich, R. & Garnier, T. (2021, August 18). Sysmon Event ID 9. Retrieved September 24, 2021. | https://docs.microsoft.com/sysinternals/downloads/sysmon#event-id-9-rawaccessread
Talos Nyetya June 2017 | Chiu, A. (2016, June 27). New Ransomware Variant "Nyetya" Compromises Systems Worldwide. Retrieved March 26, 2019. | https://blog.talosintelligence.com/2017/06/worldwide-ransomware-variant.html
Talos Sodinokibi April 2019 | Cadieux, P, et al (2019, April 30). Sodinokibi ransomware exploits WebLogic Server vulnerability. Retrieved August 4, 2020. | https://blog.talosintelligence.com/2019/04/sodinokibi-ransomware-exploits-weblogic.html
Tetra Defense Sodinokibi March 2020 | Tetra Defense. (2020, March). CAUSE AND EFFECT: SODINOKIBI RANSOMWARE ANALYSIS. Retrieved December 14, 2020. | https://www.tetradefense.com/incident-response-services/cause-and-effect-sodinokibi-ransomware-analysis
The MITRE Corporation | The MITRE Corporation The MITRE Corporation ATT&CK T1068: Exploitation for Privilege Escalation Retrieved. 2021/04/12 ATT&CK T1068: Exploitation for Privilege Escalation Retrieved. 2021/04/12 | https://attack.mitre.org/techniques/T1068/
The MITRE Corporation May 2017 | The MITRE Corporation 2017, May 31 ATT&CK T1106: Native API Retrieved. 2021/04/26 | https://attack.mitre.org/techniques/T1106/
The Office of Nuclear Reactor Regulation | The Office of Nuclear Reactor Regulation Schneider Electric 2018, January 23 TRITON - Schneider Electric Analysis and Disclosure Retrieved. 2019/03/14 Triconex Topical Report 7286-545-1 Retrieved. 2018/05/30 | https://www.nrc.gov/docs/ML1209/ML120900890.pdf
Tom Fakterman August 2019 | Tom Fakterman 2019, August 05 Sodinokibi: The Crown Prince of Ransomware Retrieved. 2021/04/12 | https://www.cybereason.com/blog/the-sodinokibi-ransomware-attack
Treasury North Korean Cyber Groups September 2019 | US Treasury . (2019, September 13). Treasury Sanctions North Korean State-Sponsored Malicious Cyber Groups. Retrieved September 29, 2021. | https://home.treasury.gov/news/press-releases/sm774
Trend Micro April 2016 | Trend Micro 2016, April 27 Malware Discovered in German Nuclear Power Plant Retrieved. 2019/10/14 | https://www.trendmicro.com/vinfo/us/security/news/cyber-attacks/malware-discovered-in-german-nuclear-power-plant
Trend Micro Cyclops Blink March 2022 | Haquebord, F. et al. (2022, March 17). Cyclops Blink Sets Sights on Asus Routers. Retrieved March 17, 2022. | https://www.trendmicro.com/en_us/research/22/c/cyclops-blink-sets-sights-on-asus-routers--.html
Trend Micro KillDisk 1 | Fernando Merces, Byron Gelera, Martin Co. (2018, June 7). KillDisk Variant Hits Latin American Finance Industry. Retrieved January 12, 2021. | https://www.trendmicro.com/en_us/research/18/f/new-killdisk-variant-hits-latin-american-financial-organizations-again.html
Trend Micro KillDisk 2 | Gilbert Sison, Rheniel Ramos, Jay Yaneza, Alfredo Oliveira. (2018, January 15). KillDisk Variant Hits Latin American Financial Groups. Retrieved January 12, 2021. | https://www.trendmicro.com/en_us/research/18/a/new-killdisk-variant-hits-financial-organizations-in-latin-america.html
Triton-EENews-2017 | Blake Sobczak. (2019, March 7). The inside story of the world’s most dangerous malware. Retrieved March 25, 2024. | https://www.eenews.net/articles/the-inside-story-of-the-worlds-most-dangerous-malware/
Twitter ItsReallyNick Masquerading Update | Carr, N.. (2018, October 25). Nick Carr Status Update Masquerading. Retrieved April 22, 2019. | https://twitter.com/ItsReallyNick/status/1055321652777619457
Tyson Macaulay | Tyson Macaulay Michael J. Assante and Robert M. Lee Corero Industrial Control System (ICS) Security Retrieved. 2019/11/04 The Industrial Control System Cyber Kill Chain Retrieved. 2019/11/04 RIoT Control: Understanding and Managing Risks and the Internet of Things Retrieved. 2019/11/04 | https://books.google.com/books?id=oXIYBAAAQBAJ&pg=PA249&lpg=PA249&dq=loss+denial+manipulation+of+view&source=bl&ots=dV1uQ8IUff&sig=ACfU3U2NIwGjhg051D_Ytw6npyEk9xcf4w&hl=en&sa=X&ved=2ahUKEwj2wJ7y4tDlAhVmplkKHSTaDnQQ6AEwAHoECAgQAQ#v=onepage&q=loss%20denial%20manipulation%20of%20view&f=false
UK GOV FSB Factsheet April 2022 | UK Gov. (2022, April 5). Russia's FSB malign activity: factsheet. Retrieved April 5, 2022. | https://www.gov.uk/government/publications/russias-fsb-malign-cyber-activity-factsheet/russias-fsb-malign-activity-factsheet
UK NCSC Olympic Attacks October 2020 | UK NCSC. (2020, October 19). UK exposes series of Russian cyber attacks against Olympic and Paralympic Games . Retrieved November 30, 2020. | https://www.gov.uk/government/news/uk-exposes-series-of-russian-cyber-attacks-against-olympic-and-paralympic-games
US District Court Indictment GRU Oct 2018 | Brady, S . (2018, October 3). Indictment - United States vs Aleksei Sergeyevich Morenets, et al.. Retrieved October 1, 2020. | https://www.justice.gov/opa/page/file/1098481/download
US District Court Indictment GRU Unit 74455 October 2020 | Scott W. Brady. (2020, October 15). United States vs. Yuriy Sergeyevich Andrienko et al.. Retrieved November 25, 2020. | https://www.justice.gov/opa/press-release/file/1328521/download
US-CERT HIDDEN COBRA June 2017 | US-CERT. (2017, June 13). Alert (TA17-164A) HIDDEN COBRA – North Korea’s DDoS Botnet Infrastructure. Retrieved July 13, 2017. | https://www.us-cert.gov/ncas/alerts/TA17-164A
US-CERT HOPLIGHT Apr 2019 | US-CERT. (2019, April 10). MAR-10135536-8 – North Korean Trojan: HOPLIGHT. Retrieved April 19, 2019. | https://www.us-cert.gov/ncas/analysis-reports/AR19-100A
US-CERT NotPetya 2017 | US-CERT. (2017, July 1). Alert (TA17-181A): Petya Ransomware. Retrieved March 15, 2019. | https://www.us-cert.gov/ncas/alerts/TA17-181A
US-CERT WannaCry 2017 | US-CERT. (2017, May 12). Alert (TA17-132A): Indicators Associated With WannaCry Ransomware. Retrieved March 25, 2019. | https://www.us-cert.gov/ncas/alerts/TA17-132A
USDOJ Sandworm Feb 2020 | Pompeo, M. (2020, February 20). The United States Condemns Russian Cyber Attack Against the Country of Georgia. Retrieved June 18, 2020. | https://2017-2021.state.gov/the-united-states-condemns-russian-cyber-attack-against-the-country-of-georgia//index.html
Ukraine15 - EISAC - 201603 | Electricity Information Sharing and Analysis Center; SANS Industrial Control Systems. (2016, March 18). Analysis of the Cyber Attack on the Ukranian Power Grid: Defense Use Case. Retrieved March 27, 2018. | https://nsarchive.gwu.edu/sites/default/files/documents/3891751/SANS-and-Electricity-Information-Sharing-and.pdf
Unit 42 Playbook Dec 2017 | Unit 42. (2017, December 15). Unit 42 Playbook Viewer. Retrieved December 20, 2017. | https://pan-unit42.github.io/playbook_viewer/
Unit 42 QUADAGENT July 2018 | Lee, B., Falcone, R. (2018, July 25). OilRig Targets Technology Service Provider and Government Agency with QUADAGENT. Retrieved August 9, 2018. | https://researchcenter.paloaltonetworks.com/2018/07/unit42-oilrig-targets-technology-service-provider-government-agency-quadagent/
Unit42 LockerGoga 2019 | Harbison, M. (2019, March 26). Born This Way? Origins of LockerGoga. Retrieved April 16, 2019. | https://unit42.paloaltonetworks.com/born-this-way-origins-of-lockergoga/
Unit42 OilRig Playbook 2023 | Unit42. (2016, May 1). Evasive Serpens Unit 42 Playbook Viewer. Retrieved February 6, 2023. | https://pan-unit42.github.io/playbook_viewer/?pb=evasive-serpens
University of Birmingham C2 | Gardiner, J., Cova, M., Nagaraja, S. (2014, February). Command & Control Understanding, Denying and Detecting. Retrieved April 20, 2016. | https://arxiv.org/ftp/arxiv/papers/1408/1408.1136.pdf
Volatility Detecting Hooks Sept 2012 | Volatility Labs. (2012, September 24). MoVP 3.1 Detecting Malware Hooks in the Windows GUI Subsystem. Retrieved December 12, 2017. | https://volatility-labs.blogspot.com/2012/09/movp-31-detecting-malware-hooks-in.html
WPXI Aliquippa Water November 2023 | WPXI. (2023, November 27). Officials investigating cyberattack on Municipal Water Authority of Aliquippa. Retrieved March 25, 2024. | https://www.wpxi.com/news/local/officials-investigating-cyberattack-municipal-water-authority-aliquippa/K5A3BEW35RAXJPMNHNE35RZ7WA/
Washington Post WannaCry 2017 | Dwoskin, E. and Adam, K. (2017, May 14). More than 150 countries affected by massive cyberattack, Europol says. Retrieved March 25, 2019. | https://www.washingtonpost.com/business/economy/more-than-150-countries-affected-by-massive-cyberattack-europol-says/2017/05/14/5091465e-3899-11e7-9e48-c4f199710b69_story.html?utm_term=.7fa16b41cad4
Wikipedia | Wikipedia Microsoft Security Response Center 2017, August Moving Beyond EMET II Windows Defender Exploit Guard Retrieved. 2020/09/25 Control-flow integrity Retrieved. 2020/09/25 | https://en.wikipedia.org/wiki/Control-flow_integrity
William Largent June 2018 | William Largent 2018, June 06 VPNFilter Update - VPNFilter exploits endpoints, targets new devices Retrieved. 2019/03/28 | https://blog.talosintelligence.com/2018/06/vpnfilter-update.html
Wireless Intrusion Detection | Tomko, A.; Rieser, C; Buell, H.; Zeret, D.; Turner, W.. (2007, March). Wireless Intrusion Detection. Retrieved September 26, 2022. | https://apps.dtic.mil/sti/pdfs/ADA466332.pdf
Wylie-22 | Jimmy Wylie. (2022, August). Analyzing PIPEDREAM: Challenges in Testing an ICS Attack Toolkit. Defcon 30. | https://media.defcon.org/DEF%20CON%2030/DEF%20CON%2030%20presentations/Jimmy%20Wylie%20-%20Analyzing%20PIPEDREAM%20Challenges%20in%20testing%20an%20ICS%20attack%20toolkit.pdf
XENOTIME | The activity group XENOTIME, as defined by Dragos, has overlaps with activity reported upon by FireEye about TEMP.Veles as well as the actors behind [TRITON](https://attack.mitre.org/software/S0609).(Citation: Dragos Xenotime 2018)(Citation: Pylos Xenotime 2019)(Citation: FireEye TRITON 2019)(Citation: FireEye TEMP.Veles 2018)
Zack Whittaker April 2017 | Zack Whittaker 2017, April 12 Dallas' emergency sirens were hacked with a rogue radio signal Retrieved. 2020/11/06 | https://www.zdnet.com/article/experts-think-they-know-how-dallas-emergency-sirens-were-hacked/
Zairon Hooking Dec 2006 | Felici, M. (2006, December 6). Any application-defined hook procedure on my machine?. Retrieved December 12, 2017. | https://zairon.wordpress.com/2006/12/06/any-application-defined-hook-procedure-on-my-machine/
iSIGHT Sandworm 2014 | Hultquist, J.. (2016, January 7). Sandworm Team and the Ukrainian Power Authority Attacks. Retrieved October 6, 2017. | https://www.fireeye.com/blog/threat-research/2016/01/ukraine-and-sandworm-team.html
split man page | Torbjorn Granlund, Richard M. Stallman. (2020, March null). split(1) — Linux manual page. Retrieved March 25, 2022. | https://man7.org/linux/man-pages/man1/split.1.html